## TP
ISO 8
RM 119/138/139
Date | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | AL/ACT # | QC SSN | Comments
2012-07-02 | 712 | 83 | 722 | 111 | 905 | 117 | 1315 | 77 | 804 | 46 | 768 | 43 |  | QC-12-06655
2012-07-12 | 469 | 39 | 156 | 16 | 167 | 12 | 2250 | 18 | 1012 | 9 | 544 | 0 |  | QC-12-07045
2012-07-20 | 112 | 12 | 287 | 52 | 198 | 8 | 222 | 32 | 476 | 89 | 423 | 46 |  | QC-12-07314
2012-07-24 | 907 | 49 | 638 | 45 | 353 | 32 | 434 | 29 | 118 | 5 | 121 | 3 |  | QC-12-07438
2012-08-06 | 189 | 11 | 391 | 10 | 260 | 16 | 163 | 15 | 193 | 9 | 181 | 9 |  | QC-12-07778
2012-08-13 | 76 | 8 | 4 | 1 | 3 | 0 | 171 | 24 | 43 | 3 | 8 | 3 |  | QC-12-07957
2012-08-22 | 394 | 28 | 508 | 16 | 178 | 6 | 350 | 12 | 201 | 2 | 105 | 10 |  | QC-12-08311
2012-09-06 | 282 | 21 | 361 | 31 | 360 | 12 | 252 | 11 | 344 | 20 | 298 | 5 |  | QC-12-08896
2012-09-12 | 1970 | 87 | 1293 | 59 | 1178 | 57 | 1821 | 75 | 1847 | 70 | 1269 | 37 |  | QC-12-09195
2012-09-19 | 1814 | 68 | 1540 | 59 | 1176 | 51 | 1322 | 60 | 1276 | 38 | 934 | 52 |  | QC-12-09485
2012-09-24 | 591 | 31 | 89 | 6 | 45 | 1 | 262 | 17 | 137 | 10 | 95 | 12 |  | QC-12-09614
2012-07-02 | 208 | 13 | 123 | 3 | 124 | 8 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-06655
2012-07-12 | 517 | 12 | 672 | 15 | 154 | 10 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07045
2012-07-20 | 17 | 3 | 22 | 1 | 21 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07314
2012-07-26 | 111 | 17 | 84 | 7 | 66 | 10 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07511
2012-08-06 | 72 | 2 | 235 | 28 | 123 | 21 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07778
2012-08-13 | 19 | 1 | 4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07957
2012-08-22 | 144 | 11 | 131 | 13 | 93 | 11 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-08311
2012-09-06 | 35 | 4 | 70 | 5 | 127 | 23 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-08896
2012-09-12 | 132 | 18 | 84 | 15 | 55 | 7 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-09195
2012-09-19 | 271 | 20 | 166 | 2 | 178 | 12 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-09485
2012-09-24 | 72 | 3 | 70 | 8 | 57 | 4 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-09614
2012-07-02 | 30 | 4 | 9 | 2 | 9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-06655
2012-07-12 | 149 | 19 | 410 | 71 | 191 | 23 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07045
2012-07-20 | 38 | 6 | 590 | 46 | 259 | 27 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07314
2012-07-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07511
2012-08-06 | 34 | 0 | 28 | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07778
2012-08-13 | 74 | 13 | 61 | 4 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07957
2012-08-22 | 31 | 7 | 23 | 3 | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-08311
2012-09-06 | 843 | 75 | 796 | 43 | 404 | 16 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-08896
2012-09-12 | 7 | 0 | 27 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-09195
2012-09-19 | 58 | 4 | 6 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-09485
2012-09-24 | 75 | 9 | 15 | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-09614
| 264 | 132
RM 128/129/129L
Date | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A1 0.5 | A1 5.0 | AL/ACT # | QC SSN | Comments
2012-07-02 | 392 | 52 | 171 | 20 | 66 | 7 | 124 | 13 | 605 | 67 | 282 | 31 | 247 | 16 | 291 | 54 | 118 | 15 | 513 | 76 | 163 | 22 | 70 | 11 | 0 | 0 |  | QC-12-06655
2012-07-13 | 19 | 2 | 2 | 0 | 1 | 0 | 72 | 0 | 59 | 3 | 27 | 1 | 27 | 1 | 4 | 0 | 4 | 0 | 25 | 4 | 7 | 0 | 7 | 0 | 0 | 0 |  | QC-12-07108
2012-07-16 | 18 | 2 | 9 | 1 | 3 | 0 | 33 | 3 | 57 | 6 | 41 | 2 | 29 | 4 | 22 | 2 | 11 | 1 | 4 | 0 | 3 | 0 | 2 | 0 | 0 | 0 |  | QC-12-07130
2012-07-23 | 17 | 4 | 13 | 4 | 10 | 0 | 9 | 1 | 47 | 11 | 122 | 7 | 23 | 0 | 12 | 2 | 6 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07396
2012-08-02 | 270 | 13 | 127 | 2 | 122 | 8 | 70 | 3 | 38 | 6 | 15 | 2 | 57 | 8 | 41 | 7 | 42 | 3 | 46 | 2 | 18 | 1 | 8 | 0 | 0 | 0 |  | QC-12-07737
2012-08-10 | 35 | 3 | 37 | 1 | 10 | 2 | 77 | 0 | 41 | 2 | 19 | 0 | 294 | 5 | 57 | 3 | 18 | 2 | 2 | 0 | 4 | 0 | 2 | 0 | 0 | 0 |  | QC-12-07898
2012-08-16 | 270 | 37 | 105 | 19 | 64 | 6 | 68 | 8 | 31 | 6 | 30 | 5 | 53 | 4 | 19 | 1 | 11 | 1 | 10 | 0 | 11 | 0 | 21 | 1 | 0 | 0 |  | QC-12-08106
2012-08-21 | 74 | 14 | 56 | 13 | 38 | 3 | 223 | 18 | 93 | 2 | 73 | 5 | 109 | 6 | 43 | 3 | 66 | 8 | 14 | 0 | 30 | 0 | 51 | 1 | 3 | 1 |  | QC-12-08259
2012-08-27 | 94 | 7 | 33 | 0 | 16 | 0 | 89 | 5 | 60 | 5 | 38 | 1 | 162 | 2 | 77 | 1 | 37 | 2 | 14 | 0 | 14 | 0 | 496 | 6 | 0 | 0 |  | QC-12-08532
2012-09-06 | 139 | 15 | 25 | 5 | 15 | 4 | 31 | 1 | 37 | 3 | 33 | 2 | 2 | 1 | 2 | 0 | 1 | 0 | 27 | 1 | 50 | 5 | 53 | 4 | 0 | 0 |  | QC-12-08896
2012-09-13 | 26 | 4 | 18 | 0 | 7 | 0 | 76 | 3 | 27 | 4 | 29 | 3 | 22 | 2 | 35 | 1 | 22 | 2 | 1 | 0 | 7 | 0 | 10 | 0 | 0 | 0 |  | QC-12-09221
2012-09-17 | 950 | 119 | 618 | 81 | 507 | 85 | 313 | 33 | 256 | 21 | 549 | 76 | 280 | 27 | 978 | 98 | 234 | 29 | 122 | 20 | 66 | 12 | 27 | 0 | 0 | 0 |  | QC-12-09411
2012-09-28 | 1350 | 60 | 859 | 37 | 406 | 23 | 70 | 6 | 34 | 2 | 40 | 5 | 186 | 14 | 118 | 12 | 77 | 4 | 14 | 0 | 5 | 1 | 14 | 0 | 0 | 0 |  | QC-12-09815
| 338 | 169
RM 134/135/135L
Date | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A1 0.5 | A1 5.0 | AL/ACT # | QC SSN | Comments
2012-07-02 | 436 | 31 | 518 | 46 | 438 | 39 | 502 | 43 | 406 | 47 | 344 | 40 | 566 | 53 | 496 | 41 | 320 | 23 | 1062 | 88 | 849 | 83 | 811 | 82 | 0 | 0 |  | QC-12-06655
2012-07-10 | 153 | 22 | 55 | 9 | 31 | 2 | 543 | 83 | 485 | 69 | 575 | 86 | 324 | 44 | 419 | 56 | 241 | 30 | 160 | 29 | 97 | 13 | 87 | 10 | 0 | 0 |  | QC-12-06953
2012-07-17 | 22 | 1 | 18 | 4 | 5 | 0 | 25 | 0 | 64 | 4 | 75 | 8 | 95 | 3 | 41 | 4 | 24 | 2 | 54 | 11 | 50 | 5 | 160 | 21 | 0 | 0 |  | QC-12-07169
2012-07-24 | 28 | 1 | 35 | 1 | 5 | 0 | 18 | 1 | 76 | 9 | 36 | 4 | 180 | 20 | 84 | 6 | 34 | 5 | 20 | 0 | 16 | 1 | 74 | 11 | 0 | 0 |  | QC-12-07438
2012-08-08 | 444 | 62 | 90 | 12 | 53 | 4 | 249 | 2 | 123 | 1 | 106 | 5 | 50 | 15 | 34 | 3 | 56 | 6 | 107 | 14 | 111 | 12 | 61 | 9 |  |  |  | QC-12-07825
2012-08-17 | 199 | 7 | 114 | 5 | 232 | 48 | 225 | 5 | 103 | 1 | 130 | 8 | 71 | 7 | 39 | 3 | 29 | 3 | 48 | 8 | 16 | 3 | 19 | 5 |  |  |  | QC-12-08160
2012-08-20 | 7 | 1 | 10 | 2 | 5 | 1 | 47 | 9 | 124 | 16 | 91 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 10 | 100 | 17 | 95 | 16 |  |  |  | QC-12-08246
| 176 | 88
RM 136/137
Date | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | AL/ACT # | QC SSN | Comments
2012-07-02 | 186 | 21 | 95 | 18 | 35 | 1 | 190 | 26 | 127 | 21 | 101 | 13 |  | QC-12-06655
2012-07-10 | 44 | 4 | 43 | 11 | 22 | 3 | 128 | 26 | 75 | 12 | 25 | 2 |  | QC-12-06953
2012-07-17 | 105 | 2 | 50 | 1 | 22 | 3 | 92 | 3 | 26 | 1 | 18 | 1 |  | QC-12-07169
2012-07-24 | 22 | 2 | 26 | 3 | 8 | 1 | 41 | 4 | 16 | 2 | 7 | 0 |  | QC-12-07438
2012-07-31 | 110 | 3 | 70 | 4 | 32 | 0 | 124 | 12 | 36 | 3 | 17 | 1 |  | QC-12-07598
2012-08-08 | 251 | 12 | 229 | 16 | 131 | 7 | 162 | 6 | 67 | 6 | 63 | 9 |  | QC-12-07825
2012-08-17 | 182 | 6 | 106 | 1 | 125 | 14 | 46 | 9 | 68 | 5 | 38 | 2 |  | QC-12-08160
2012-08-20 | 36 | 5 | 44 | 5 | 45 | 5 | 138 | 9 | 58 | 4 | 58 | 5 |  | QC-12-08246
2012-08-31 | 62 | 11 | 49 | 5 | 195 | 17 | 58 | 7 | 62 | 4 | 47 | 5 |  | QC-12-08706
2012-09-06 | 137 | 6 | 90 | 0 | 58 | 0 | 137 | 4 | 70 | 2 | 51 | 2 |  | QC-12-08896
2012-09-14 | 37 | 5 | 55 | 4 | 37 | 2 | 45 | 14 | 33 | 3 | 60 | 3 |  | QC-12-09349
2012-09-17 | 9 | 1 | 6 | 1 | 21 | 2 | 60 | 5 | 70 | 5 | 44 | 2 |  | QC-12-09411
2012-09-28 | 63 | 19 | 99 | 20 | 67 | 12 | 69 | 10 | 88 | 12 | 120 | 7 |  | QC-12-09815
2012-07-02 | 107 | 12 | 181 | 37 | 95 | 16 | 197 | 20 | 133 | 22 | 90 | 9 |  | QC-12-06655
2012-07-10 | 26 | 2 | 35 | 1 | 23 | 3 | 219 | 25 | 87 | 10 | 52 | 3 |  | QC-12-06953
2012-07-17 | 59 | 2 | 66 | 1 | 19 | 1 | 280 | 5 | 170 | 4 | 46 | 2 |  | QC-12-07169
2012-07-24 | 7 | 1 | 10 | 0 | 7 | 1 | 94 | 15 | 62 | 9 | 26 | 1 |  | QC-12-07438
2012-07-31 | 38 | 2 | 65 | 2 | 69 | 1 | 138 | 5 | 139 | 5 | 207 | 3 |  | QC-12-07598
2012-08-08 | 32 | 7 | 85 | 10 | 156 | 4 | 3 | 1 | 2 | 0 | 88 | 4 |  | QC-12-07825
2012-08-17 | 53 | 8 | 51 | 5 | 37 | 2 | 30 | 4 | 13 | 2 | 7 | 1 |  | QC-12-08160
2012-08-20 | 37 | 5 | 8 | 1 | 19 | 4 | 10 | 0 | 14 | 1 | 27 | 1 |  | QC-12-08246
2012-08-31 | 615 | 8 | 265 | 6 | 150 | 1 | 11 | 2 | 0 | 0 | 3 | 0 |  | QC-12-08706
2012-09-06 | 45 | 3 | 31 | 0 | 28 | 1 | 110 | 16 | 37 | 3 | 30 | 4 |  | QC-12-08896
2012-09-14 | 0 | 0 | 0 | 0 | 8 | 1 | 97 | 10 | 71 | 9 | 37 | 4 |  | QC-12-09349
2012-09-17 | 37 | 5 | 7 | 0 | 5 | 0 | 20 | 2 | 97 | 4 | 138 | 2 |  | QC-12-09411
2012-09-28 | 8 | 3 | 12 | 1 | 10 | 0 | 415 | 37 | 176 | 21 | 123 | 11 |  | QC-12-09815
| 312 | 156
RM 140/151/150
Date | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | AL/ACT # | QC SSN | Comments
2012-07-02 | 28 | 4 | 44 | 5 | 34 | 0 |  | QC-12-06655
2012-07-11 | 65 | 7 | 30 | 0 | 17 | 0 |  | QC-12- 07005
2012-07-19 | 10 | 0 | 16 | 1 | 23 | 0 |  | QC-12-07246
2012-07-27 | 82 | 14 | 28 | 3 | 63 | 2 |  | QC-12-07527
2012-08-09 | 43 | 5 | 32 | 3 | 297 | 2 |  | QC-12-07889
2012-08-15 | 57 | 2 | 32 | 2 | 46 | 1 |  | QC-12-08051
2012-08-24 | 303 | 38 | 159 | 13 | 147 | 18 |  | QC-12-08446
2012-08-30 | 306 | 35 | 149 | 18 | 110 | 8 |  | QC-12-08673
2012-09-05 | 145 | 20 | 97 | 17 | 94 | 14 |  | QC-12-08848
2012-09-10 | 33 | 6 | 14 | 3 | 3 | 0 |  | QC-12-09046
2012-09-21 | 19 | 4 | 30 | 1 | 36 | 3 |  | QC-12-09571
2012-09-24 | 11 | 0 | 11 | 1 | 43 | 4 |  | QC-12-09614
2012-07-02 | 101 | 23 | 89 | 20 | 93 | 11 |  | QC-12-06655
2012-07-11 | 186 | 18 | 54 | 7 | 46 | 7 |  | QC-12- 07005
2012-07-19 | 78 | 7 | 55 | 3 | 35 | 4 |  | QC-12-07246
2012-07-27 | 243 | 12 | 310 | 13 | 31 | 1 |  | QC-12-07527
2012-08-09 | 190 | 25 | 226 | 28 | 395 | 41 |  | QC-12-07889
2012-08-15 | 28 | 3 | 33 | 2 | 26 | 1 |  | QC-12-08051
2012-08-24 | 221 | 27 | 227 | 27 | 251 | 18 |  | QC-12-08446
2012-08-30 | 44 | 8 | 202 | 14 | 178 | 25 |  | QC-12-08673
2012-09-05 | 99 | 13 | 131 | 13 | 66 | 6 |  | QC-12-08848
2012-09-10 | 202 | 15 | 84 | 5 | 40 | 9 |  | QC-12-09046
2012-09-21 | 37 | 6 | 19 | 2 | 9 | 0 |  | QC-12-09571
2012-09-24 | 58 | 6 | 65 | 3 | 18 | 2 |  | QC-12-09614
2012-07-02 | 232 | 15 | 196 | 19 | 119 | 5 |  | QC-12-06655
2012-07-11 | 153 | 11 | 46 | 3 | 28 | 4 |  | QC-12- 07005
2012-07-19 | 47 | 6 | 32 | 1 | 36 | 3 |  | QC-12-07246
2012-07-27 | 63 | 2 | 45 | 1 | 29 | 3 |  | QC-12-07527
2012-08-09 | 339 | 13 | 144 | 12 | 212 | 11 |  | QC-12-07889
2012-08-15 | 81 | 4 | 43 | 2 | 22 | 2 |  | QC-12-08051
2012-08-24 | 175 | 12 | 111 | 8 | 188 | 21 |  | QC-12-08446
2012-08-30 | 468 | 71 | 207 | 21 | 87 | 8 |  | QC-12-08673
2012-09-05 | 152 | 18 | 132 | 20 | 118 | 12 |  | QC-12-08848
2012-09-10 | 39 | 1 | 73 | 2 | 386 | 82 |  | QC-12-09046
2012-09-21 | 44 | 3 | 21 | 2 | 12 | 1 |  | QC-12-09571
2012-09-24 | 67 | 6 | 56 | 2 | 13 | 0 |  | QC-12-09614
| 216 | 108
RM 141/141L
Date | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A1 0.5 | A1 5.0 | AL/ACT # | QC SSN | Comments
2012-07-02 | 22 | 2 | 10 | 2 | 8 | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 37 | 5 | 39 | 5 | 46 | 1 | 0 | 0 |  | QC-12-06655
2012-07-11 | 138 | 16 | 286 | 23 | 294 | 26 | 11 | 2 | 128 | 37 | 67 | 12 | 46 | 4 | 64 | 3 | 34 | 5 | 0 | 0 |  | QC-12-07005
2012-07-19 | 32 | 7 | 15 | 2 | 3 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 25 | 1 | 22 | 5 | 0 | 0 |  | QC-12-07246
2012-07-27 | 221 | 9 | 8 | 0 | 72 | 2 | 46 | 3 | 108 | 7 | 36 | 5 | 10 | 0 | 27 | 0 | 3 | 0 | 0 | 0 |  | QC-12-07527
2012-08-03 | 241 | 32 | 386 | 55 | 222 | 27 | 10 | 1 | 5 | 1 | 15 | 4 | 165 | 19 | 150 | 18 | 140 | 19 | 0 | 0 |  | QC-12-07765
2012-08-09 | 49 | 4 | 31 | 2 | 17 | 0 | 55 | 5 | 26 | 4 | 93 | 11 | 20 | 2 | 10 | 0 | 14 | 0 | 0 | 0 |  | QC-12-07889
2012-08-15 | 84 | 7 | 31 | 3 | 17 | 1 | 22 | 0 | 6 | 0 | 1 | 0 | 76 | 9 | 74 | 9 | 17 | 4 | 0 | 0 |  | QC-12-08051
2012-08-24 | 80 | 5 | 73 | 5 | 83 | 10 | 35 | 2 | 14 | 1 | 8 | 1 | 44 | 10 | 50 | 6 | 65 | 7 | 0 | 0 |  | QC-12-08446
2012-08-30 | 45 | 16 | 244 | 13 | 119 | 10 | 14 | 3 | 34 | 4 | 29 | 2 | 11 | 3 | 9 | 1 | 3 | 0 | 0 | 0 |  | QC-12-08673
2012-09-05 | 42 | 3 | 48 | 8 | 63 | 12 | 34 | 6 | 60 | 10 | 35 | 1 | 55 | 16 | 128 | 17 | 92 | 5 | 0 | 0 |  | QC-12-08848
2012-09-10 | 28 | 11 | 160 | 8 | 46 | 6 | 4 | 1 | 106 | 1 | 14 | 2 | 8 | 1 | 8 | 0 | 6 | 0 | 0 | 0 |  | QC-12-09046
2012-09-21 | 53 | 1 | 15 | 2 | 1 | 0 | 6 | 0 | 2 | 1 | 4 | 1 | 153 | 2 | 48 | 0 | 43 | 1 | 0 | 0 |  | QC-12-09571
2012-09-26 | 43 | 4 | 11 | 4 | 8 | 0 | 15 | 0 | 7 | 0 | 4 | 1 | 28 | 2 | 18 | 3 | 14 | 1 | 0 | 0 |  | QC-12-09680
| 260 | 130
RM 160/161
Date | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | AL/ACT # | QC SSN | Comments
2012-07-02 | 6 | 0 | 1 | 0 | 0 | 0 | 104 | 1 | 73 | 1 | 20 | 0 | 86 | 1 | 27 | 2 | 7 | 0 | 7 | 1 | 16 | 1 | 16 | 0 |  | QC-12-06655
2012-07-09 | 21 | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 194 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 4 | 0 | 7 | 2 |  | QC-12-06834
2012-07-18 | 66 | 6 | 8 | 0 | 128 | 15 | 11 | 1 | 3 | 1 | 4 | 0 | 40 | 15 | 24 | 1 | 223 | 6 | 23 | 5 | 36 | 3 | 47 | 3 |  | QC-12-07207
2012-07-25 | 249 | 6 | 11 | 1 | 37 | 5 | 16 | 2 | 21 | 6 | 81 | 14 | 15 | 0 | 29 | 5 | 49 | 4 | 3 | 0 | 9 | 1 | 14 | 1 |  | QC-12-07465
2012-08-08 | 365 | 27 | 747 | 32 | 931 | 115 | 1 | 0 | 23 | 4 | 2 | 0 | 324 | 6 | 106 | 8 | 12 | 1 | 8 | 1 | 0 | 0 | 0 | 0 |  | QC-12-07825
2012-08-17 | 51 | 3 | 46 | 7 | 101 | 18 | 58 | 14 | 349 | 17 | 106 | 9 | 82 | 10 | 32 | 4 | 42 | 5 | 38 | 2 | 154 | 9 | 115 | 13 |  | QC-12-08160
2012-08-20 | 31 | 6 | 13 | 2 | 13 | 1 | 11 | 3 | 10 | 3 | 49 | 4 | 32 | 2 | 29 | 2 | 14 | 1 | 10 | 2 | 0 | 0 | 1 | 1 |  | QC-12-08246
2012-08-31 | 68 | 5 | 79 | 12 | 47 | 3 | 15 | 1 | 12 | 1 | 16 | 1 | 14 | 0 | 16 | 2 | 37 | 3 | 34 | 2 | 26 | 0 | 21 | 1 |  | QC-12-08706
2012-09-07 | 289 | 11 | 25 | 2 | 13 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 173 | 15 | 108 | 5 | 27 | 2 | 30 | 1 | 6 | 1 |  | QC-12-09019
2012-09-14 | 121 | 2 | 8 | 0 | 10 | 2 | 67 | 9 | 23 | 4 | 70 | 7 | 2 | 0 | 9 | 1 | 24 | 2 | 38 | 6 | 23 | 0 | 42 | 8 |  | QC-12-09349
2012-09-17 | 46 | 1 | 6 | 0 | 0 | 0 | 16 | 1 | 327 | 13 | 58 | 1 | 41 | 3 | 29 | 2 | 30 | 2 | 9 | 1 | 8 | 0 | 73 | 0 |  | QC-12-09411
2012-09-25 | 30 | 6 | 18 | 1 | 12 | 0 | 26 | 3 | 18 | 4 | 37 | 2 | 70 | 3 | 40 | 2 | 51 | 2 | 71 | 1 | 54 | 1 | 26 | 2 |  | QC-12-09646
| 288 | 144
RM 162/163/147B
Date | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | AL/ACT # | QC SSN | Comments
2012-07-02 | 73 | 0 | 49 | 3 | 35 | 3 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-06655
2012-07-11 | 296 | 48 | 391 | 43 | 288 | 48 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12- 07005
2012-07-19 | 17 | 1 | 15 | 2 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07246
2012-07-27 | 85 | 7 | 48 | 3 | 36 | 2 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07527
2012-08-03 | 21 | 2 | 23 | 1 | 56 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07765
2012-08-09 | 22 | 3 | 7 | 1 | 12 | 2 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07889
2012-08-15 | 40 | 3 | 120 | 2 | 18 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-08051
2012-08-24 | 388 | 32 | 308 | 24 | 270 | 24 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-08446
2012-08-30 | 209 | 4 | 439 | 13 | 292 | 3 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-08673
2012-09-05 | 24 | 2 | 36 | 3 | 18 | 4 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-08848
2012-09-10 | 93 | 11 | 171 | 24 | 64 | 8 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-09046
2012-09-21 | 83 | 5 | 79 | 4 | 70 | 4 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-09571
2012-09-26 | 98 | 6 | 161 | 4 | 126 | 2 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-09680
2012-07-02 | 60 | 6 | 271 | 5 | 97 | 2 | 17 | 0 | 102 | 0 | 37 | 4 |  | QC-12-06655
2012-07-11 | 93 | 7 | 135 | 13 | 150 | 10 | 47 | 5 | 49 | 6 | 53 | 1 |  | QC-12- 07005
2012-07-19 | 563 | 16 | 234 | 12 | 24 | 1 | 25 | 3 | 23 | 1 | 6 | 1 |  | QC-12-07246
2012-07-27 | 37 | 1 | 35 | 1 | 30 | 1 | 56 | 6 | 34 | 9 | 113 | 5 |  | QC-12-07527
2012-08-03 | 37 | 4 | 49 | 5 | 42 | 3 | 776 | 21 | 674 | 24 | 607 | 24 |  | QC-12-07765
2012-08-09 | 321 | 8 | 157 | 4 | 140 | 5 | 1145 | 34 | 450 | 8 | 101 | 2 |  | QC-12-07889
2012-08-15 | 103 | 6 | 207 | 8 | 69 | 0 | 488 | 13 | 466 | 7 | 391 | 4 |  | QC-12-08051
2012-08-24 | 108 | 11 | 96 | 12 | 51 | 4 | 4 | 0 | 7 | 1 | 4 | 0 |  | QC-12-08446
2012-08-30 | 140 | 3 | 146 | 3 | 217 | 4 | 413 | 11 | 372 | 12 | 303 | 2 |  | QC-12-08673
2012-09-05 | 40 | 4 | 27 | 1 | 27 | 2 | 4 | 0 | 5 | 0 | 0 | 0 |  | QC-12-08848
2012-09-10 | 283 | 13 | 224 | 10 | 904 | 40 | 71 | 3 | 77 | 2 | 31 | 3 |  | QC-12-09046
2012-09-21 | 23 | 4 | 33 | 3 | 152 | 12 | 16 | 2 | 26 | 1 | 40 | 2 |  | QC-12-09571
2012-09-26 | 51 | 5 | 57 | 5 | 137 | 13 | 406 | 2 | 375 | 13 | 366 | 10 |  | QC-12-09680
2012-07-02 | 64 | 7 | 39 | 5 | 56 | 4 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-06655
2012-07-11 | 111 | 13 | 23 | 2 | 34 | 2 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12- 07005
2012-07-19 | 56 | 6 | 18 | 2 | 9 | 2 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07246
2012-07-27 | 47 | 3 | 37 | 5 | 28 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07527
2012-08-03 | 1168 | 29 | 698 | 12 | 528 | 12 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07765
2012-08-09 | 79 | 5 | 28 | 4 | 26 | 3 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07889
2012-08-15 | 287 | 8 | 237 | 2 | 184 | 6 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-08051
2012-08-24 | 51 | 9 | 28 | 3 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-08446
2012-08-30 | 101 | 6 | 48 | 2 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-08673
2012-09-05 | 79 | 4 | 21 | 4 | 15 | 4 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-08848
2012-09-10 | 9 | 1 | 6 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-09046
2012-09-21 | 39 | 2 | 16 | 0 | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-09571
2012-09-26 | 312 | 26 | 202 | 14 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-09680
| 312 | 156
ISO 7
RM 126/127/127L
Date | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A1 0.5 | A1 5.0 | AL/ACT # | QC SSN | Comments
2012-07-02 | 620 | 21 | 336 | 19 | 406 | 10 | 292 | 21 | 91 | 3 | 121 | 5 | 16 | 1 | 11 | 1 | 4 | 0 | 35 | 2 | 27 | 1 | 83 | 2 | 0 | 0 |  | QC-12-06655
2012-07-06 | 73 | 5 | 31 | 1 | 21 | 1 | 20 | 2 | 16 | 2 | 13 | 3 | 122 | 12 | 54 | 2 | 14 | 0 | 19 | 0 | 14 | 1 | 10 | 0 | 0 | 0 |  | QC-12-06807
2012-07-10 | 75 | 11 | 64 | 5 | 33 | 6 | 38 | 4 | 55 | 1 | 153 | 4 | 9 | 2 | 72 | 2 | 90 | 2 | 20 | 3 | 49 | 0 | 152 | 4 | 0 | 0 |  | QC-12-06953
2012-07-11 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07005
2012-07-12 | 154 | 6 | 114 | 5 | 120 | 2 | 391 | 10 | 184 | 6 | 258 | 8 | 183 | 6 | 137 | 6 | 186 | 6 | 483 | 4 | 447 | 24 | 359 | 27 | 0 | 0 |  | QC-12-07058 | Pre
2012-07-12 | 69 | 1 | 89 | 7 | 158 | 10 | 75 | 4 | 158 | 8 | 141 | 10 | 73 | 7 | 77 | 6 | 193 | 7 | 112 | 9 | 165 | 5 | 265 | 9 | 0 | 0 |  | QC-12-07058 | Post
2012-07-17 | 17 | 1 | 16 | 4 | 10 | 0 | 9 | 1 | 163 | 4 | 64 | 1 | 97 | 1 | 89 | 2 | 48 | 0 | 82 | 2 | 23 | 0 | 17 | 0 | 0 | 0 |  | QC-12-07169
2012-07-20 | 146 | 2 | 134 | 6 | 67 | 5 | 70 | 4 | 51 | 5 | 43 | 0 | 4 | 0 | 162 | 3 | 62 | 3 | 30 | 2 | 20 | 1 | 13 | 1 | 0 | 0 |  | QC-12-07314
2012-07-24 | 31 | 2 | 17 | 2 | 13 | 1 | 12 | 0 | 53 | 6 | 54 | 1 | 203 | 9 | 54 | 3 | 32 | 0 | 41 | 2 | 17 | 1 | 7 | 1 | 1 | 0 |  | QC-12-07438
2012-07-26 | 28 | 4 | 23 | 0 | 14 | 0 | 21 | 1 | 79 | 1 | 72 | 2 | 91 | 1 | 44 | 4 | 19 | 3 | 32 | 3 | 17 | 0 | 8 | 0 | 0 | 0 |  | QC-12-07511
2012-07-31 | 83 | 5 | 51 | 7 | 46 | 7 | 147 | 2 | 91 | 1 | 57 | 5 | 68 | 1 | 56 | 1 | 19 | 0 | 56 | 3 | 29 | 3 | 14 | 0 | 0 | 0 |  | QC-12-07598
2012-08-06 | 339 | 23 | 268 | 22 | 185 | 13 | 194 | 2 | 49 | 0 | 29 | 0 | 102 | 7 | 38 | 5 | 14 | 1 | 128 | 17 | 105 | 6 | 37 | 3 | 0 | 0 |  | QC-12-07778
2012-08-08 | 304 | 19 | 285 | 23 | 283 | 14 | 206 | 8 | 446 | 33 | 156 | 16 | 10 | 0 | 2 | 0 | 52 | 6 | 90 | 8 | 50 | 5 | 40 | 4 | 2 | 2 |  | QC-12-07825
2012-08-13 | 93 | 13 | 55 | 10 | 39 | 4 | 39 | 0 | 28 | 1 | 171 | 17 | 86 | 12 | 39 | 4 | 62 | 10 | 69 | 6 | 55 | 2 | 81 | 9 | 0 | 0 |  | QC-12-07957
2012-08-17 | 15 | 0 | 32 | 6 | 34 | 6 | 13 | 3 | 11 | 0 | 31 | 4 | 105 | 17 | 158 | 20 | 192 | 24 | 34 | 4 | 42 | 4 | 39 | 1 | 0 | 0 |  | QC-12-08160
2012-08-20 | 51 | 8 | 58 | 11 | 49 | 6 | 24 | 4 | 23 | 5 | 65 | 4 | 30 | 4 | 5 | 0 | 79 | 18 | 36 | 3 | 31 | 0 | 37 | 2 | 0 | 0 |  | QC-12-08246
2012-08-22 | 60 | 3 | 28 | 3 | 24 | 1 | 153 | 4 | 119 | 4 | 50 | 1 | 46 | 1 | 28 | 4 | 22 | 0 | 36 | 4 | 9 | 1 | 5 | 0 | 0 | 0 |  | QC-12-08311
2012-08-31 | 27 | 5 | 21 | 3 | 19 | 0 | 96 | 7 | 46 | 1 | 45 | 2 | 18 | 0 | 34 | 6 | 42 | 2 | 32 | 2 | 18 | 2 | 15 | 0 | 0 | 0 |  | QC-12-08706
2012-09-04 | 17 | 0 | 23 | 1 | 19 | 0 | 7 | 1 | 3 | 1 | 1 | 0 | 5 | 1 | 0 | 0 | 1 | 0 | 14 | 3 | 5 | 1 | 2 | 0 | 1 | 0 |  | QC-12-08819
2012-09-07 | 141 | 20 | 94 | 19 | 48 | 10 | 42 | 1 | 47 | 1 | 82 | 3 | 48 | 1 | 27 | 1 | 34 | 4 | 222 | 7 | 113 | 3 | 53 | 4 | 0 | 0 |  | QC-12-09019
2012-09-12 | 120 | 27 | 83 | 15 | 66 | 14 | 211 | 38 | 48 | 9 | 66 | 13 | 47 | 3 | 58 | 8 | 36 | 5 | 61 | 12 | 22 | 4 | 13 | 4 | 0 | 0 |  | QC-12-09195
2012-09-14 | 243 | 47 | 145 | 14 | 100 | 11 | 84 | 2 | 34 | 1 | 28 | 4 | 14 | 4 | 9 | 0 | 3 | 0 | 53 | 6 | 11 | 2 | 7 | 0 | 0 | 0 |  | QC-12-09349
2012-09-17 | 721 | 45 | 212 | 13 | 91 | 9 | 292 | 25 | 278 | 23 | 371 | 33 | 415 | 34 | 182 | 11 | 231 | 15 | 436 | 34 | 141 | 11 | 63 | 5 | 0 | 0 |  | QC-12-09411
2012-09-18 | 17 | 1 | 7 | 0 | 6 | 0 | 33 | 0 | 15 | 2 | 8 | 2 | 377 | 8 | 31 | 1 | 24 | 0 | 14 | 2 | 9 | 0 | 12 | 0 | 0 | 0 |  | QC-12-09457
2012-09-24 | 23 | 4 | 13 | 0 | 25 | 2 | 509 | 6 | 112 | 1 | 102 | 1 | 120 | 4 | 48 | 1 | 42 | 0 | 25 | 1 | 14 | 0 | 15 | 0 | 0 | 0 |  | QC-12-09614
2012-09-25 | 39 | 2 | 45 | 0 | 66 | 7 | 271 | 6 | 159 | 0 | 86 | 2 | 30 | 4 | 15 | 0 | 18 | 1 | 64 | 6 | 41 | 3 | 56 | 2 | 0 | 0 |  | QC-12-09646
| 670 | 335
| 652 | 326
RM 130/131/131L
Date | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A1 0.5 | A1 5.0 | AL/ACT # | QC SSN | Comments
2012-07-02 | 140 | 18 | 50 | 3 | 38 | 6 | 146 | 25 | 117 | 15 | 219 | 22 | 39 | 10 | 31 | 2 | 17 | 1 | 25 | 4 | 62 | 14 | 62 | 9 | 0 | 0 |  | QC-12-06655
2012-07-05 | 48 | 21 | 36 | 13 | 12 | 2 | 16 | 8 | 9 | 1 | 9 | 1 | 209 | 31 | 117 | 17 | 43 | 5 | 18 | 0 | 54 | 3 | 12 | 0 | 0 | 0 |  | QC-12-06765
2012-07-09 | 206 | 11 | 48 | 1 | 36 | 0 | 54 | 4 | 13 | 1 | 12 | 2 | 22 | 2 | 15 | 1 | 11 | 0 | 11 | 0 | 15 | 0 | 26 | 0 | 2 | 1 |  | QC-12-06834
2012-07-12 | 26 | 3 | 9 | 1 | 7 | 1 | 68 | 11 | 81 | 12 | 116 | 12 | 136 | 11 | 66 | 6 | 19 | 1 | 7 | 1 | 36 | 8 | 14 | 3 | 0 | 0 |  | QC-12-07045
2012-07-18 | 222 | 41 | 59 | 11 | 51 | 16 | 27 | 4 | 20 | 4 | 7 | 1 | 8 | 1 | 13 | 1 | 27 | 4 | 48 | 2 | 37 | 3 | 39 | 6 | 8 | 2 |  | QC-12-07207
2012-07-20 | 34 | 3 | 15 | 0 | 38 | 2 | 87 | 7 | 112 | 5 | 69 | 3 | 37 | 2 | 39 | 6 | 23 | 0 | 6 | 0 | 2 | 0 | 0 | 0 | 0 | 0 |  | QC-12-07314
2012-07-25 | 39 | 12 | 11 | 3 | 21 | 0 | 129 | 12 | 61 | 4 | 25 | 0 | 55 | 3 | 19 | 3 | 126 | 11 | 44 | 3 | 57 | 4 | 24 | 3 | 0 | 0 |  | QC-12-07465
2012-07-26 | 164 | 12 | 26 | 0 | 19 | 3 | 58 | 4 | 67 | 0 | 23 | 1 | 54 | 3 | 28 | 2 | 20 | 1 | 8 | 0 | 84 | 1 | 92 | 2 | 0 | 0 |  | QC-12-07511
2012-07-31 | 25 | 3 | 4 | 0 | 0 | 0 | 50 | 4 | 17 | 1 | 44 | 5 | 49 | 3 | 16 | 2 | 17 | 3 | 17 | 1 | 12 | 1 | 26 | 2 | 0 | 0 |  | QC-12-07598
2012-08-06 | 262 | 18 | 196 | 15 | 491 | 44 | 118 | 11 | 104 | 12 | 259 | 24 | 349 | 47 | 99 | 7 | 46 | 4 | 371 | 34 | 186 | 19 | 169 | 13 | 7 | 2 |  | QC-12-07778
2012-08-07 | 88 | 45 | 17 | 4 | 4 | 0 | 381 | 26 | 642 | 35 | 861 | 41 | 387 | 16 | 169 | 12 | 145 | 16 | 175 | 11 | 112 | 5 | 22 | 0 | 0 | 0 |  | QC-12-07802
2012-08-13 | 42 | 4 | 27 | 0 | 13 | 1 | 172 | 15 | 70 | 4 | 538 | 46 | 47 | 7 | 34 | 0 | 48 | 6 | 43 | 4 | 14 | 1 | 14 | 1 | 4 | 2 |  | QC-12-07957
2012-08-14 | 76 | 18 | 33 | 7 | 21 | 2 | 49 | 3 | 52 | 3 | 106 | 8 | 119 | 4 | 39 | 4 | 5 | 0 | 26 | 3 | 52 | 0 | 39 | 5 | 0 | 0 |  | QC-12-08007
2012-08-21 | 20 | 10 | 5 | 1 | 3 | 0 | 241 | 15 | 76 | 10 | 105 | 8 | 245 | 25 | 294 | 35 | 137 | 15 | 171 | 15 | 174 | 10 | 248 | 29 | 0 | 0 |  | QC-12-08259
2012-08-22 | 290 | 49 | 88 | 20 | 25 | 3 | 61 | 2 | 27 | 3 | 24 | 2 | 71 | 5 | 53 | 6 | 28 | 1 | 10 | 0 | 8 | 0 | 7 | 1 | 0 | 0 |  | QC-12-08311
2012-08-28 | 71 | 6 | 39 | 8 | 12 | 1 | 124 | 16 | 64 | 9 | 38 | 4 | 222 | 21 | 297 | 31 | 267 | 27 | 96 | 5 | 77 | 6 | 91 | 5 | 1 | 1 |  | QC-12-08570
2012-08-29 | 92 | 13 | 43 | 7 | 40 | 8 | 68 | 4 | 46 | 4 | 30 | 2 | 113 | 8 | 38 | 1 | 26 | 2 | 0 | 0 | 14 | 1 | 10 | 0 | 0 | 0 |  | QC-12-08628
2012-09-04 | 133 | 23 | 44 | 7 | 18 | 2 | 25 | 4 | 26 | 4 | 1 | 0 | 106 | 13 | 158 | 7 | 93 | 5 | 1 | 0 | 2 | 0 | 3 | 1 | 0 | 0 |  | QC-12-08819
2012-09-07 | 23 | 7 | 7 | 3 | 2 | 0 | 183 | 37 | 128 | 30 | 77 | 19 | 8 | 3 | 40 | 4 | 59 | 8 | 60 | 2 | 25 | 4 | 14 | 1 | 0 | 0 |  | QC-12-09019
2012-09-11 | 64 | 13 | 30 | 3 | 13 | 1 | 45 | 8 | 114 | 10 | 419 | 28 | 143 | 19 | 114 | 11 | 68 | 8 | 0 | 0 | 5 | 0 | 7 | 1 | 0 | 0 |  | QC-12-09154
2012-09-12 | 350 | 40 | 91 | 7 | 40 | 2 | 43 | 3 | 28 | 4 | 123 | 27 | 20 | 1 | 197 | 10 | 133 | 13 | 47 | 3 | 17 | 2 | 7 | 1 | 0 | 0 |  | QC-12-09195
2012-09-17 | 487 | 43 | 409 | 42 | 241 | 23 | 224 | 27 | 194 | 16 | 146 | 25 | 300 | 30 | 135 | 11 | 151 | 9 | 72 | 3 | 37 | 2 | 22 | 0 | 0 | 0 |  | QC-12-09411
2012-09-19 | 52 | 4 | 44 | 6 | 4 | 0 | 443 | 21 | 166 | 17 | 217 | 20 | 93 | 6 | 31 | 1 | 31 | 3 | 9 | 2 | 1 | 0 | 3 | 0 | 0 | 0 |  | QC-12-09485
2012-09-20 | 40 | 8 | 25 | 7 | 8 | 2 | 79 | 9 | 83 | 7 | 49 | 5 | 31 | 4 | 12 | 1 | 74 | 4 | 13 | 0 | 19 | 0 | 10 | 2 | 0 | 0 |  | QC-12-09544
2012-09-24 | 35 | 5 | 14 | 0 | 18 | 0 | 124 | 8 | 29 | 2 | 11 | 0 | 100 | 16 | 60 | 6 | 37 | 3 | 1 | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | QC-12-09614
2012-09-25 | 1 | 0 | 9 | 1 | 10 | 1 | 142 | 7 | 54 | 2 | 20 | 0 | 18 | 0 | 2 | 0 | 23 | 2 | 1 | 0 | 2 | 0 | 3 | 0 | 0 | 0 |  | QC-12-09646
| 676 | 338
RM 132/133/133L
Date | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A1 0.5 | A1 5.0 | AL/ACT # | QC SSN | Comments
2012-07-02 | 115 | 18 | 26 | 5 | 87 | 8 | 189 | 22 | 108 | 7 | 44 | 4 | 193 | 22 | 216 | 28 | 183 | 30 | 88 | 6 | 133 | 10 | 204 | 40 | 0 | 0 |  | QC-12-06655
2012-07-05 | 67 | 5 | 52 | 13 | 16 | 2 | 5 | 0 | 9 | 0 | 24 | 1 | 118 | 15 | 49 | 3 | 112 | 14 | 92 | 15 | 31 | 2 | 89 | 10 | 0 | 0 |  | QC-12-06765
2012-07-09 | 2 | 0 | 1 | 0 | 1 | 0 | 512 | 46 | 805 | 64 | 563 | 59 | 3937 | 562 | 2143 | 249 | 3607 | 516 | 750 | 101 | 839 | 123 | 332 | 30 | 0 | 0 | ACT-20120034 | QC-12-06834
2012-07-12 | 62 | 10 | 28 | 3 | 60 | 13 | 18 | 4 | 266 | 17 | 604 | 14 | 196 | 31 | 42 | 5 | 20 | 2 | 24 | 1 | 4 | 0 | 10 | 0 | 0 | 0 |  | QC-12-07045
2012-07-18 | 659 | 52 | 271 | 21 | 151 | 15 | 159 | 16 | 19 | 2 | 137 | 2 | 33 | 5 | 49 | 5 | 25 | 1 | 7 | 1 | 27 | 1 | 35 | 3 | 0 | 0 | AL-073012-001 | QC-12-07207
2012-07-20 | 12 | 3 | 6 | 0 | 4 | 0 | 11 | 1 | 4 | 2 | 23 | 5 | 78 | 10 | 53 | 7 | 21 | 3 | 16 | 1 | 16 | 2 | 284 | 12 | 0 | 0 |  | QC-12-07314
2012-07-25 | 11 | 3 | 2 | 2 | 3 | 0 | 404 | 38 | 177 | 9 | 110 | 13 | 278 | 22 | 93 | 10 | 94 | 2 | 288 | 22 | 210 | 9 | 297 | 15 | 0 | 0 |  | QC-12-07465
2012-07-26 | 15 | 0 | 5 | 0 | 2 | 1 | 492 | 19 | 409 | 25 | 211 | 15 | 462 | 22 | 269 | 10 | 378 | 10 | 441 | 30 | 499 | 38 | 400 | 16 | 0 | 0 |  | QC-12-07511
2012-07-31 | 7 | 0 | 1 | 0 | 2 | 0 | 151 | 12 | 68 | 8 | 70 | 7 | 169 | 21 | 82 | 5 | 65 | 2 | 173 | 45 | 118 | 20 | 98 | 11 | 0 | 0 |  | QC-12-07598
2012-08-07 | 72 | 12 | 20 | 1 | 19 | 2 | 16 | 1 | 16 | 2 | 23 | 0 | 97 | 8 | 53 | 6 | 47 | 4 | 32 | 1 | 23 | 0 | 20 | 0 | 0 | 0 |  | QC-12-07802
2012-08-10 | 0 | 0 | 1 | 0 | 0 | 0 | 124 | 6 | 127 | 15 | 156 | 14 | 781 | 68 | 737 | 35 | 316 | 21 | 90 | 16 | 272 | 30 | 428 | 40 | 0 | 0 |  | QC-12-07898
2012-08-14 | 4 | 1 | 15 | 3 | 9 | 1 | 20 | 0 | 8 | 0 | 15 | 0 | 122 | 7 | 145 | 8 | 91 | 3 | 27 | 0 | 9 | 0 | 12 | 0 | 0 | 0 |  | QC-12-08007
2012-08-16 | 1 | 0 | 1 | 0 | 0 | 0 | 44 | 2 | 73 | 1 | 50 | 5 | 8 | 1 | 17 | 1 | 7 | 0 | 8 | 1 | 17 | 1 | 7 | 0 | 0 | 0 |  | QC-12-08106
2012-08-21 | 8 | 1 | 4 | 1 | 0 | 0 | 15 | 0 | 95 | 10 | 43 | 12 | 154 | 25 | 117 | 22 | 97 | 20 | 32 | 8 | 34 | 3 | 33 | 5 | 0 | 0 |  | QC-12-08259
2012-08-23 | 898 | 29 | 373 | 10 | 218 | 7 | 24 | 5 | 45 | 5 | 18 | 4 | 27 | 6 | 32 | 5 | 59 | 12 | 29 | 3 | 23 | 5 | 27 | 3 | 0 | 0 |  | QC-12-08410
2012-08-27 | 18 | 1 | 11 | 1 | 7 | 0 | 102 | 34 | 80 | 27 | 49 | 15 | 263 | 79 | 230 | 71 | 221 | 68 | 201 | 79 | 174 | 58 | 180 | 50 | 0 | 0 | ACT-20120066 | QC-12-08532
2012-08-28 | 20 | 7 | 6 | 1 | 0 | 0 | 27 | 1 | 88 | 3 | 202 | 5 | 105 | 10 | 82 | 3 | 54 | 5 | 43 | 3 | 39 | 2 | 51 | 2 | 0 | 0 |  | QC-12-08570
2012-08-29 | 18 | 1 | 12 | 0 | 9 | 0 | 7 | 0 | 43 | 2 | 35 | 2 | 47 | 2 | 37 | 0 | 44 | 2 | 56 | 1 | 32 | 0 | 27 | 0 | 0 | 0 |  | QC-12-08628
2012-09-04 | 24 | 4 | 21 | 2 | 1 | 0 | 510 | 24 | 43 | 3 | 12 | 0 | 18 | 1 | 6 | 1 | 9 | 0 | 7 | 0 | 2 | 0 | 3 | 0 | 0 | 0 |  | QC-12-08819
2012-09-06 | 219 | 15 | 127 | 22 | 161 | 49 | 10 | 0 | 6 | 0 | 5 | 0 | 65 | 4 | 38 | 1 | 17 | 0 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 0 |  | QC-12-08896
2012-09-11 | 164 | 10 | 104 | 6 | 101 | 5 | 191 | 12 | 117 | 13 | 62 | 7 | 135 | 10 | 121 | 13 | 97 | 9 | 132 | 17 | 107 | 11 | 66 | 2 | 0 | 0 |  | QC-12-09154
2012-09-13 | 10 | 1 | 1 | 0 | 3 | 0 | 31 | 1 | 26 | 0 | 10 | 0 | 96 | 5 | 54 | 3 | 35 | 1 | 21 | 2 | 17 | 1 | 49 | 3 | 0 | 0 |  | QC-12-09221
2012-09-17 | 151 | 13 | 111 | 14 | 77 | 8 | 34 | 2 | 0 | 0 | 3 | 0 | 119 | 28 | 111 | 13 | 111 | 8 | 7 | 0 | 5 | 0 | 16 | 2 | 0 | 0 |  | QC-12-09411
2012-09-20 | 10 | 2 | 3 | 0 | 5 | 1 | 20 | 3 | 15 | 1 | 34 | 1 | 29 | 1 | 28 | 4 | 24 | 1 | 84 | 2 | 48 | 0 | 52 | 0 | 4 | 0 |  | QC-12-09544
2012-09-25 | 219 | 31 | 133 | 17 | 99 | 10 | 24 | 3 | 5 | 0 | 0 | 0 | 69 | 6 | 22 | 1 | 30 | 5 | 44 | 5 | 24 | 3 | 8 | 0 | 0 | 0 |  | QC-12-09646
2012-09-27 | 5 | 0 | 5 | 0 | 3 | 0 | 16 | 1 | 32 | 4 | 160 | 12 | 87 | 9 | 111 | 12 | 26 | 5 | 18 | 8 | 17 | 3 | 20 | 2 | 0 | 0 |  | QC-12-09746
| 676 | 338
RM 152/156
Date | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | AL/ACT # | QC SSN | Comments
2012-07-02 | 280 | 47 | 42 | 5 | 6 | 1 | 165 | 22 | 30 | 7 | 7 | 0 | 70 | 11 | 37 | 1 | 13 | 0 | 52 | 6 | 76 | 7 | 33 | 2 |  | QC-12-06655
2012-07-06 | 30 | 3 | 3 | 0 | 19 | 3 | 36 | 4 | 37 | 6 | 45 | 6 | 103 | 10 | 60 | 6 | 109 | 13 | 113 | 12 | 109 | 6 | 257 | 45 |  | QC-12-06807
2012-07-09 | 51 | 7 | 7 | 2 | 41 | 0 | 71 | 0 | 38 | 1 | 23 | 1 | 26 | 1 | 2 | 0 | 17 | 1 | 49 | 8 | 37 | 11 | 15 | 3 |  | QC-12-06834
2012-07-13 | 64 | 16 | 27 | 13 | 3 | 1 | 7 | 1 | 7 | 1 | 6 | 0 | 37 | 3 | 18 | 1 | 9 | 0 | 20 | 0 | 4 | 0 | 1 | 0 |  | QC-12-07108
2012-07-16 | 34 | 7 | 16 | 7 | 3 | 0 | 74 | 3 | 19 | 3 | 15 | 3 | 36 | 4 | 47 | 5 | 11 | 1 | 31 | 5 | 17 | 3 | 123 | 20 |  | QC-12-07130
2012-07-18 | 180 | 34 | 88 | 17 | 38 | 5 | 8 | 2 | 61 | 2 | 175 | 8 | 12 | 2 | 9 | 3 | 441 | 43 | 406 | 28 | 127 | 8 | 56 | 0 |  | QC-12-07207
2012-07-23 | 26 | 8 | 3 | 1 | 1 | 0 | 0 | 0 | 12 | 0 | 3 | 0 | 22 | 0 | 8 | 0 | 4 | 1 | 11 | 1 | 19 | 1 | 11 | 1 |  | QC-12-07396
2012-07-25 | 169 | 42 | 155 | 38 | 63 | 25 | 30 | 1 | 126 | 13 | 92 | 10 | 211 | 12 | 212 | 27 | 133 | 14 | 168 | 13 | 110 | 16 | 66 | 3 |  | QC-12-07465
2012-08-02 | 707 | 30 | 497 | 30 | 108 | 4 | 36 | 0 | 39 | 5 | 22 | 4 | 9 | 0 | 4 | 1 | 51 | 3 | 249 | 24 | 106 | 16 | 69 | 4 |  | QC-12-07737
2012-08-07 | 35 | 8 | 2 | 0 | 7 | 3 | 8 | 0 | 5 | 1 | 67 | 4 | 32 | 6 | 90 | 21 | 81 | 8 | 27 | 3 | 4 | 1 | 3 | 0 |  | QC-12-07802
2012-08-10 | 9 | 2 | 2 | 0 | 1 | 0 | 26 | 1 | 61 | 1 | 19 | 1 | 33 | 0 | 11 | 0 | 6 | 1 | 4 | 0 | 5 | 0 | 6 | 0 |  | QC-12-07898
2012-08-14 | 30 | 8 | 17 | 6 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 1 | 70 | 2 | 157 | 6 | 36 | 1 | 3 | 0 | 2 | 0 |  | QC-12-08007
2012-08-16 | 27 | 3 | 10 | 1 | 23 | 8 | 21 | 0 | 92 | 4 | 13 | 3 | 11 | 1 | 0 | 0 | 0 | 0 | 5 | 0 | 1 | 0 | 4 | 0 |  | QC-12-08106
2012-08-21 | 27 | 9 | 11 | 3 | 8 | 2 | 4 | 0 | 4 | 0 | 2 | 0 | 4 | 0 | 30 | 2 | 51 | 5 | 134 | 12 | 68 | 5 | 35 | 2 |  | QC-12-08259
2012-08-23 | 368 | 21 | 120 | 7 | 45 | 6 | 41 | 1 | 24 | 4 | 8 | 2 | 0 | 0 | 2 | 1 | 21 | 3 | 168 | 14 | 51 | 2 | 66 | 3 |  | QC-12-08410
2012-08-27 | 62 | 9 | 62 | 1 | 2 | 0 | 6 | 0 | 6 | 0 | 21 | 0 | 2 | 0 | 14 | 0 | 21 | 2 | 15 | 2 | 4 | 0 | 5 | 0 |  | QC-12-08532
2012-08-28 | 65 | 19 | 22 | 3 | 2 | 1 | 131 | 24 | 41 | 2 | 7 | 0 | 0 | 0 | 1 | 0 | 21 | 0 | 110 | 8 | 99 | 6 | 108 | 8 |  | QC-12-08570
2012-08-29 | 34 | 5 | 15 | 4 | 1 | 0 | 9 | 1 | 0 | 0 | 0 | 0 | 109 | 0 | 4 | 0 | 2 | 0 | 28 | 5 | 12 | 1 | 18 | 0 |  | QC-12-08628
2012-09-04 | 118 | 16 | 59 | 3 | 8 | 1 | 3 | 1 | 3 | 1 | 2 | 1 | 9 | 1 | 0 | 0 | 1 | 0 | 6 | 3 | 1 | 0 | 0 | 0 |  | QC-12-08819
2012-09-07 | 167 | 23 | 17 | 0 | 10 | 3 | 12 | 2 | 23 | 2 | 54 | 5 | 234 | 34 | 172 | 17 | 251 | 28 | 92 | 9 | 56 | 5 | 119 | 21 |  | QC-12-09019
2012-09-11 | 72 | 8 | 38 | 3 | 16 | 0 | 4 | 0 | 12 | 1 | 6 | 0 | 28 | 1 | 15 | 1 | 3 | 0 | 20 | 7 | 75 | 14 | 89 | 8 |  | QC-12-09154
2012-09-13 | 44 | 9 | 13 | 1 | 0 | 0 | 18 | 0 | 6 | 1 | 13 | 1 | 34 | 2 | 35 | 2 | 12 | 0 | 24 | 5 | 9 | 1 | 7 | 1 |  | QC-12-09221
2012-09-17 | 85 | 2 | 29 | 1 | 12 | 1 | 62 | 6 | 29 | 1 | 38 | 2 | 52 | 2 | 29 | 0 | 15 | 0 | 243 | 19 | 243 | 22 | 124 | 8 |  | QC-12-09411
2012-09-20 | 123 | 17 | 44 | 4 | 13 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 66 | 5 | 185 | 5 | 124 | 5 | 74 | 5 | 39 | 6 |  | QC-12-09544
2012-09-27 | 36 | 7 | 8 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 12 | 2 | 8 | 0 | 71 | 5 | 35 | 1 | 27 | 2 |  | QC-12-09746
2012-09-28 | 886 | 39 | 218 | 5 | 123 | 10 | 16 | 0 | 7 | 0 | 6 | 0 | 28 | 3 | 108 | 8 | 37 | 2 | 38 | 6 | 26 | 2 | 75 | 3 |  | QC-12-09815
| 624 | 312
RM 154/153/153L
Date | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A3 0.5 | A3 5.0 | A1 0.5 | A1 5.0 | AL/ACT # | QC SSN | Comments
2012-07-02 | 130 | 20 | 33 | 11 | 6 | 4 | 449 | 43 | 101 | 11 | 62 | 6 | 294 | 40 | 148 | 20 | 301 | 47 | 242 | 28 | 76 | 12 | 51 | 12 | 0 | 0 |  | QC-12-06655
2012-07-06 | 54 | 1 | 10 | 0 | 17 | 2 | 8 | 0 | 53 | 1 | 15 | 0 | 35 | 3 | 45 | 3 | 26 | 0 | 33 | 0 | 33 | 3 | 25 | 1 | 1 | 1 |  | QC-12-06807
2012-07-10 | 233 | 44 | 47 | 7 | 21 | 2 | 91 | 8 | 39 | 7 | 6 | 1 | 61 | 5 | 76 | 8 | 71 | 9 | 89 | 8 | 8 | 0 | 5 | 2 | 0 | 0 |  | QC-12-06953
2012-07-13 | 110 | 16 | 21 | 1 | 23 | 5 | 32 | 6 | 19 | 2 | 18 | 2 | 3 | 1 | 9 | 3 | 8 | 0 | 47 | 6 | 2 | 1 | 1 | 0 | 0 | 0 |  | QC-12-07108
2012-07-16 | 90 | 20 | 47 | 10 | 18 | 0 | 88 | 7 | 38 | 4 | 37 | 4 | 144 | 11 | 87 | 9 | 10 | 1 | 58 | 12 | 12 | 1 | 16 | 3 | 0 | 0 |  | QC-12-07130
2012-07-17 | 343 | 39 | 77 | 9 | 35 | 1 | 12 | 1 | 10 | 1 | 158 | 8 | 62 | 6 | 27 | 1 | 66 | 7 | 52 | 4 | 11 | 0 | 11 | 0 | 2 | 0 |  | QC-12-07169
2012-07-23 | 379 | 28 | 113 | 13 | 47 | 3 | 90 | 2 | 8 | 0 | 25 | 1 | 15 | 1 | 16 | 1 | 46 | 6 | 33 | 6 | 9 | 0 | 2 | 0 | 0 | 0 |  | QC-12-07396
2012-07-24 | 274 | 38 | 50 | 4 | 28 | 5 | 200 | 14 | 54 | 2 | 247 | 17 | 168 | 18 | 58 | 2 | 136 | 7 | 55 | 3 | 14 | 0 | 18 | 0 | 0 | 0 |  | QC-12-07438
2012-08-02 | 316 | 29 | 177 | 14 | 73 | 7 | 290 | 22 | 345 | 20 | 70 | 4 | 129 | 15 | 60 | 8 | 200 | 30 | 88 | 14 | 25 | 2 | 75 | 12 | 0 | 0 |  | QC-12-07737
2012-08-06 | 138 | 12 | 41 | 4 | 12 | 0 | 213 | 14 | 35 | 2 | 27 | 8 | 44 | 2 | 140 | 14 | 127 | 15 | 70 | 10 | 122 | 17 | 69 | 10 | 0 | 0 |  | QC-12-07778
2012-08-07 | 206 | 36 | 77 | 8 | 64 | 8 | 92 | 6 | 114 | 16 | 102 | 25 | 65 | 10 | 22 | 5 | 107 | 17 | 190 | 19 | 127 | 14 | 152 | 10 | 0 | 0 |  | QC-12-07802
2012-08-13 | 221 | 25 | 77 | 10 | 79 | 5 | 134 | 12 | 69 | 11 | 28 | 5 | 72 | 6 | 9 | 2 | 3 | 0 | 52 | 7 | 51 | 7 | 46 | 6 | 0 | 0 |  | QC-12-07957
2012-08-14 | 273 | 41 | 41 | 5 | 7 | 1 | 54 | 3 | 52 | 4 | 9 | 1 | 73 | 8 | 16 | 2 | 15 | 2 | 31 | 1 | 10 | 0 | 7 | 0 | 0 | 0 |  | QC-12-08007
2012-08-22 | 79 | 15 | 29 | 1 | 11 | 0 | 10 | 1 | 30 | 5 | 12 | 0 | 19 | 2 | 32 | 3 | 19 | 1 | 33 | 4 | 5 | 0 | 1 | 0 | 0 | 0 |  | QC-12-08311
2012-08-23 | 216 | 9 | 51 | 0 | 22 | 1 | 49 | 7 | 15 | 3 | 5 | 2 | 14 | 1 | 12 | 2 | 4 | 1 | 143 | 0 | 173 | 6 | 92 | 3 | 1 | 0 |  | QC-12-08410
2012-08-28 | 57 | 14 | 38 | 6 | 76 | 14 | 25 | 2 | 9 | 0 | 13 | 2 | 11 | 2 | 9 | 0 | 54 | 3 | 20 | 0 | 10 | 0 | 11 | 0 | 0 | 0 |  | QC-12-08570
2012-08-29 | 355 | 67 | 82 | 20 | 25 | 5 | 215 | 23 | 50 | 1 | 7 | 0 | 146 | 19 | 98 | 8 | 33 | 2 | 56 | 6 | 13 | 1 | 13 | 1 | 0 | 0 |  | QC-12-08628
2012-08-30 | 488 | 15 | 103 | 8 | 42 | 2 | 227 | 28 | 60 | 3 | 35 | 1 | 130 | 25 | 158 | 23 | 28 | 1 | 60 | 8 | 19 | 6 | 14 | 2 | 0 | 0 |  | QC-12-08673
2012-08-31 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 3 | 37 | 5 | 58 | 5 | 67 | 8 | 43 | 5 | 164 | 18 | 96 | 6 | 38 | 2 | 26 | 0 | 0 | 0 |  | QC-12-08706
2012-09-04 | 71 | 9 | 76 | 7 | 43 | 3 | 639 | 20 | 579 | 35 | 42 | 11 | 41 | 4 | 14 | 3 | 18 | 2 | 66 | 10 | 43 | 7 | 14 | 1 | 0 | 0 |  | QC-12-08819
2012-09-07 | 129 | 29 | 38 | 13 | 25 | 7 | 144 | 16 | 103 | 10 | 52 | 9 | 46 | 4 | 2 | 0 | 17 | 5 | 39 | 5 | 64 | 8 | 13 | 1 | 0 | 0 |  | QC-12-09019
2012-09-11 | 236 | 45 | 59 | 8 | 57 | 9 | 13 | 2 | 2 | 0 | 6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 5 | 0 | 5 | 1 | 0 | 0 |  | QC-12-09154
2012-09-12 | 105 | 18 | 16 | 4 | 13 | 4 | 57 | 4 | 24 | 1 | 34 | 5 | 162 | 20 | 134 | 7 | 41 | 3 | 215 | 17 | 82 | 9 | 75 | 5 | 0 | 0 |  | QC-12-09195
2012-09-14 | 137 | 12 | 55 | 2 | 11 | 1 | 45 | 2 | 63 | 7 | 83 | 6 | 51 | 5 | 8 | 1 | 18 | 4 | 51 | 3 | 20 | 1 | 104 | 5 | 0 | 0 |  | QC-12-09349
2012-09-17 | 563 | 9 | 387 | 7 | 264 | 15 | 5 | 1 | 28 | 2 | 457 | 29 | 70 | 14 | 199 | 24 | 424 | 32 | 10 | 0 | 25 | 3 | 5 | 0 | 0 | 0 |  | QC-12-09411
2012-09-20 | 144 | 19 | 99 | 11 | 66 | 7 | 57 | 9 | 22 | 3 | 30 | 4 | 16 | 2 | 37 | 1 | 3 | 0 | 27 | 2 | 28 | 1 | 22 | 1 | 0 | 0 |  | QC-12-09544
2012-09-27 | 119 | 21 | 110 | 8 | 91 | 14 | 8 | 0 | 6 | 0 | 24 | 1 | 9 | 1 | 1 | 0 | 0 | 0 | 41 | 7 | 18 | 1 | 10 | 2 | 0 | 0 |  | QC-12-09746
2012-09-28 | 99 | 10 | 75 | 8 | 26 | 0 | 27 | 7 | 12 | 1 | 9 | 0 | 8 | 0 | 4 | 0 | 2 | 0 | 10 | 1 | 18 | 3 | 9 | 2 | 0 | 0 |  | QC-12-09815
| 728 | 364
RM 157/158/159
Date | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | A2 0.5 | A2 5.0 | AL/ACT # | QC SSN | Comments
2012-07-02 | 151 | 8 | 68 | 8 | 14 | 2 | 327 | 12 | 27 | 0 | 44 | 0 | 3 | 0 | 9 | 0 | 0 | 0 | 8 | 1 |  | QC-12-06655
2012-07-03 | 0 | 0 | 1 | 0 | 0 | 0 | 1325 | 86 | 1 | 0 | 22 | 7 | 1 | 0 | 6 | 1 | 202 | 2 | 27 | 1 |  | QC-12-06750
2012-07-11 | 248 | 26 | 72 | 15 | 19 | 3 | 1428 | 87 | 4 | 0 | 5 | 2 | 2 | 0 | 10 | 1 | 3 | 1 | 4 | 1 |  | QC-12- 07005
2012-07-13 | 5 | 1 | 24 | 0 | 34 | 2 | 482 | 15 | 3 | 0 | 2 | 0 | 3 | 1 | 3 | 1 | 2 | 0 | 0 | 0 |  | QC-12-07108
2012-07-16 | 0 | 0 | 0 | 0 | 0 | 0 | 1305 | 98 | 2 | 1 | 12 | 0 | 0 | 0 | 6 | 1 | 1 | 0 | 0 | 0 |  | QC-12-07130
2012-07-19 | 31 | 5 | 12 | 1 | 1 | 0 | 146 | 8 | 18 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 3 | 0 | 0 | 0 |  | QC-12-07246
2012-07-23 | 0 | 0 | 0 | 0 | 0 | 0 | 695 | 29 | 1 | 0 | 2 | 0 | 1 | 0 | 4 | 1 | 1 | 0 | 0 | 0 |  | QC-12-07396
2012-07-27 | 15 | 1 | 114 | 7 | 27 | 3 | 231 | 44 | 12 | 0 | 9 | 0 | 4 | 0 | 39 | 3 | 37 | 1 | 54 | 2 |  | QC-12-07527
2012-08-02 | 402 | 27 | 36 | 3 | 36 | 5 | 2196 | 191 | 11 | 0 | 14 | 1 | 39 | 4 | 4 | 0 | 5 | 0 | 6 | 2 |  | QC-12-07737
2012-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 894 | 58 | 12 | 2 | 4 | 1 | 5 | 3 | 1 | 0 | 5 | 0 | 0 | 0 |  | QC-12-07765
2012-08-09 | 0 | 0 | 0 | 0 | 0 | 0 | 897 | 27 | 2 | 0 | 3 | 0 | 0 | 0 | 57 | 7 | 89 | 4 | 51 | 4 |  | QC-12-07889
2012-08-10 | 3 | 1 | 5 | 2 | 14 | 2 | 326 | 14 | 10 | 0 | 2 | 0 | 0 | 0 | 18 | 1 | 3 | 0 | 0 | 0 |  | QC-12-07898
2012-08-15 | 0 | 0 | 2 | 1 | 0 | 0 | 272 | 11 | 22 | 1 | 4 | 0 | 0 | 0 | 18 | 1 | 2 | 1 | 0 | 0 |  | QC-12-08051
2012-08-23 | 106 | 11 | 133 | 7 | 10 | 0 | 157 | 20 | 14 | 3 | 15 | 5 | 3 | 0 | 5 | 0 | 0 | 0 | 0 | 0 |  | QC-12-08410
| 280 | 140
Aseptic Core
RM 143/144/145
Date | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A2 0.5 | A2 5.0 | A1 0.5 | A1 5.0 | A2 0.5 | A2 5.0 | A3 0.5 | A3 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | A1 0.5 | A1 5.0 | AL/ACT # | QC SSN | Comments
2012-07-02 | 40 | 1 | 75 | 4 | 25 | 1 | 130 | 3 | 855 | 71 | 1501 | 90 | 1680 | 84 | 24 | 5 | 18 | 4 | 11 | 0 |  | QC-12-06655
2012-07-03 | 4 | 1 | 0 | 0 | 2 | 0 | 254 | 11 | 463 | 27 | 390 | 24 | 356 | 24 | 4 | 0 | 5 | 1 | 3 | 0 |  | QC-12-06696
2012-07-10 | 12 | 1 | 2 | 0 | 1 | 0 | 666 | 82 | 141 | 7 | 764 | 52 | 208 | 7 | 9 | 1 | 20 | 2 | 5 | 0 |  | QC-12-06909
2012-07-13 | 58 | 11 | 13 | 1 | 4 | 0 | 448 | 49 | 115 | 10 | 576 | 30 | 67 | 4 | 15 | 2 | 5 | 0 | 11 | 2 |  | QC-12-07113
2012-07-16 | 82 | 3 | 73 | 15 | 138 | 11 | 759 | 32 | 256 | 20 | 910 | 34 | 302 | 24 | 118 | 12 | 63 | 5 | 74 | 9 |  | QC-12-07122
2012-07-18 | 1 | 0 | 0 | 0 | 0 | 0 | 49 | 5 | 491 | 27 | 411 | 31 | 426 | 21 | 35 | 7 | 48 | 4 | 48 | 2 |  | QC-12-07194
2012-07-23 | 12 | 0 | 13 | 1 | 1 | 0 | 20 | 5 | 243 | 50 | 1825 | 61 | 625 | 61 | 20 | 2 | 118 | 0 | 29 | 1 |  | QC-12-07398
2012-07-25 | 53 | 3 | 278 | 20 | 51 | 2 | 278 | 15 | 4074 | 226 | 135 | 4 | 716 | 41 | 20 | 3 | 29 | 2 | 13 | 0 |  | QC-12-07466
2012-07-31 | 3 | 0 | 7 | 0 | 7 | 1 | 193 | 9 | 1441 | 74 | 1924 | 98 | 555 | 16 | 50 | 8 | 29 | 1 | 21 | 1 |  | QC-12-07627
2012-08-01 | 150 | 8 | 60 | 1 | 33 | 0 | 317 | 17 | 783 | 51 | 2582 | 238 | 122 | 12 | 1 | 0 | 4 | 0 | 4 | 0 |  | QC-12-07674
2012-08-07 | 133 | 10 | 73 | 2 | 46 | 3 | 113 | 7 | 2024 | 140 | 2581 | 164 | 1417 | 90 | 107 | 8 | 81 | 7 | 60 | 7 |  | QC-12-07809
2012-08-09 | 24 | 1 | 11 | 0 | 20 | 1 | 198 | 10 | 1611 | 70 | 2475 | 113 | 659 | 35 | 94 | 8 | 32 | 2 | 13 | 1 |  | QC-12-07894
2012-08-13 | 71 | 2 | 2 | 0 | 0 | 0 | 320 | 10 | 617 | 65 | 1728 | 76 | 974 | 66 | 70 | 9 | 43 | 2 | 15 | 0 |  | QC-12-07961
2012-08-16 | 126 | 1 | 129 | 6 | 207 | 6 | 475 | 26 | 2752 | 69 | 2708 | 36 | 918 | 25 | 46 | 1 | 35 | 2 | 24 | 3 |  | QC-12-08084
2012-08-23 | 16 | 0 | 4 | 0 | 6 | 0 | 277 | 25 | 1025 | 53 | 1930 | 100 | 1167 | 95 | 49 | 9 | 36 | 8 | 8 | 2 |  | QC-12-08416
2012-08-24 | 377 | 18 | 113 | 14 | 56 | 10 | 2312 | 167 | 554 | 18 | 179 | 9 | 1449 | 68 | 119 | 16 | 33 | 4 | 10 | 1 |  | QC-12-08482
2012-08-28 | 81 | 0 | 31 | 0 | 21 | 1 | 340 | 4 | 577 | 12 | 996 | 29 | 253 | 21 | 19 | 2 | 7 | 1 | 10 | 0 |  | QC-12-08548
2012-08-30 | 80 | 4 | 100 | 7 | 36 | 1 | 144 | 1 | 54 | 0 | 420 | 16 | 1921 | 71 | 19 | 0 | 20 | 0 | 12 | 0 |  | QC-12-08683
2012-09-04 | 589 | 18 | 333 | 11 | 250 | 5 | 129 | 3 | 109 | 4 | 257 | 20 | 947 | 50 | 36 | 5 | 12 | 2 | 36 | 0 |  | QC-12-08821
2012-09-05 | 64 | 11 | 440 | 12 | 232 | 3 | 2469 | 118 | 735 | 38 | 1640 | 67 | 256 | 4 | 64 | 5 | 30 | 0 | 24 | 0 |  | QC-12-08854
2012-09-10 | 10 | 4 | 45 | 7 | 4 | 1 | 387 | 32 | 334 | 13 | 1133 | 65 | 548 | 28 | 363 | 9 | 99 | 5 | 20 | 0 |  | QC-12-09062
2012-09-11 | 14 | 0 | 6 | 0 | 63 | 2 | 866 | 91 | 324 | 30 | 31 | 2 | 384 | 34 | 1 | 0 | 1 | 0 | 21 | 0 |  | QC-12-09120
2012-09-18 | 7 | 0 | 49 | 1 | 34 | 0 | 172 | 4 | 1211 | 22 | 2154 | 57 | 439 | 12 | 44 | 3 | 10 | 0 | 35 | 1 |  | QC-12-09448
2012-09-21 | 78 | 1 | 119 | 2 | 17 | 0 | 131 | 12 | 737 | 20 | 2507 | 82 | 1895 | 27 | 28 | 0 | 8 | 1 | 10 | 1 |  | QC-12-09573
2012-09-24 | 25 | 2 | 32 | 4 | 48 | 4 | 145 | 6 | 466 | 30 | 1534 | 132 | 1690 | 101 | 25 | 1 | 9 | 1 | 1 | 0 |  | QC-12-09631
2012-09-26 | 38 | 7 | 61 | 6 | 57 | 6 | 299 | 27 | 199 | 14 | 1137 | 152 | 462 | 46 | 7 | 1 | 5 | 0 | 15 | 0 |  | QC-12-09682
| 520 | 260

## AV
ISO 8
RM 119/138/139 | TAMC | TAMC | Gram Stain/
Date | A1 | A2 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-12 | 0 | 0 | [5 empty] | QC-12-07045
2012-07-20 | 0 | 0 | [5 empty] | QC-12-07314
2012-07-24 | 2 | 3 | 3 | 2 |  |  |  | QC-12-07438
2012-07-30 | 0 | 0 | [5 empty] | QC-12-07587 | SDA
2012-08-06 | 0 | 0 | [5 empty] | QC-12-07778
2012-08-13 | 0 | 0 | [5 empty] | QC-12-07957
2012-08-22 | 4 | 0 | 1 | 3 |  |  |  | QC-12-08311
2012-09-06 | 0 | 1 | 1 |  |  |  |  | QC-12-08896
2012-09-12 | 3 | 1 | 4 |  |  |  |  | QC-12-09195
2012-09-19 | 11 | 9 | 11 | 9 |  |  |  | QC-12-09485
2012-09-24 | 2 | 3 | 3 | 2 |  |  |  | QC-12-09614
2012-07-02 | 0 | [6 empty] | QC-12-06655
2012-07-12 | 0 | [6 empty] | QC-12-07045
2012-07-20 | 2 |  | 2 |  |  |  |  | QC-12-07314
2012-07-26 | 3 |  | 2 |  |  |  |  | QC-12-07511 | Dark brown mold
2012-07-30 | 0 | [6 empty] | QC-12-07587 | SDA
2012-08-06 | 0 | [6 empty] | QC-12-07778
2012-08-13 | 0 | [6 empty] | QC-12-07957
2012-08-22 | 2 |  |  | 2 |  |  |  | QC-12-08311
2012-09-06 | 2 |  |  | 2 |  |  |  | QC-12-08896
2012-09-12 | 1 |  | 1 |  |  |  |  | QC-12-09195
2012-09-19 | 3 |  | 3 |  |  |  |  | QC-12-09485
2012-09-24 | 1 |  | 1 |  |  |  |  | QC-12-09614
2012-07-02 | 0 | [6 empty] | QC-12-06655
2012-07-12 | 0 | [6 empty] | QC-12-07045
2012-07-20 | 0 | [6 empty] | QC-12-07314
2012-07-26 | 4 |  | 2 | 2 |  |  |  | QC-12-07511
2012-07-30 | 0 | [6 empty] | QC-12-07587 | SDA
2012-08-06 | 0 | [6 empty] | QC-12-07778
2012-08-13 | 0 | [6 empty] | QC-12-07957
2012-08-22 | 0 | [6 empty] | QC-12-08311
2012-09-06 | 4 |  | 2 | 2 |  |  |  | QC-12-08896
2012-09-12 | 1 |  | 1 |  |  |  |  | QC-12-09195
2012-09-19 | 0 | [6 empty] | QC-12-09485
2012-09-24 | 1 |  | 1 |  |  |  |  | QC-12-09614
| 48 |  | 38 | 24 | 0 | 0
RM 128/129/129L | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | A1 | A1 | A2 | A3 | A1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-13 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07108
2012-07-16 | 0 | 6 | 0 | 0 | 0 |  |  |  | 6 |  | QC-12-07130 | yeast
2012-07-23 | 2 | 3 | 4 | 0 | 0 | 9 |  |  |  |  | QC-12-07396
2012-08-02 | 1 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-07737
2012-08-03 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07738 | SDA
2012-08-10 | 0 | 1 | 1 | 0 | 0 |  | 2 |  |  |  | QC-12-07898
2012-08-16 | 9 | 4 | 1 | 0 | 0 | 14 |  |  |  |  | QC-12-08106
2012-08-21 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08259
2012-08-27 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08532
2012-09-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08896
2012-09-13 | 0 | 0 | 1 | 0 | 0 | 1 |  |  |  |  | QC-12-09221
2012-09-17 | 1 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-09411
2012-09-28 | 0 | 2 | 3 | 0 | 0 | 4 | 1 |  |  |  | QC-12-09815
| 70 |  |  |  |  | 28 | 5 | 0 | 6
RM 134/135/135L | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | A1 | A1 | A2 | A3 | A1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-10 | 31 | 25 | 24 | 23 | 0 | 98 |  |  | 5 | AL-072012-001 | QC-12-06953 | (white, fibrous)
2012-07-17 | 3 | 0 | 0 | 1 | 0 |  | 4 |  |  |  | QC-12-07169
2012-07-24 | 0 | 0 | 1 | 1 | 0 | 1 | 1 |  |  |  | QC-12-07438
2012-07-30 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07587 | SDA
2012-08-08 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07825
2012-08-17 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08160
2012-08-20 | 1 | 16 | 0 | 4 |  | 16 | 5 |  |  |  | QC-12-08246
| 37 |  |  |  |  | 115 | 10 | 0 | 5
RM 136/137 | TAMC | TAMC | Gram Stain/
Date | A1 | A2 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-10 | 13 | 22 | 35 |  |  |  |  | QC-12-06953
2012-07-17 | 2 | 1 | 1 | 2 |  |  |  | QC-12-07169
2012-07-24 | 0 | 0 | [5 empty] | QC-12-07438
2012-07-31 | 1 | 0 | 1 |  |  |  |  | QC-12-07598
2012-07-31 | 0 | 0 | [5 empty] | QC-12-07599 | SDA
2012-08-08 | 0 | 0 | [5 empty] | QC-12-07825
2012-08-17 | 0 | 0 | [5 empty] | QC-12-08160
2012-08-20 | 14 | 8 | 11 | 11 |  |  |  | QC-12-08246
2012-08-31 | 2 | 1 | 3 |  |  |  |  | QC-12-08706
2012-09-06 | 0 | 1 | 1 |  |  |  |  | QC-12-08896
2012-09-14 | 0 | 0 | [5 empty] | QC-12-09349
2012-09-17 | 1 | 0 | 1 |  |  |  |  | QC-12-09411
2012-09-28 | 0 | 0 | [5 empty] | QC-12-09815
2012-07-02 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-10 | 5 | 0 | 5 |  |  |  |  | QC-12-06953
2012-07-17 | 0 | 0 | [5 empty] | QC-12-07169
2012-07-24 | 0 | 0 | [5 empty] | QC-12-07438
2012-07-31 | 2 | 1 | 2 | 1 |  |  |  | QC-12-07598
2012-07-31 | 0 | 0 | [5 empty] | QC-12-07599 | SDA
2012-08-08 | 0 | 0 | [5 empty] | QC-12-07825
2012-08-17 | 0 | 0 | [5 empty] | QC-12-08160
2012-08-20 | 0 | 6 | 6 |  |  |  |  | QC-12-08246
2012-08-31 | 0 | 0 | [5 empty] | QC-12-08706
2012-09-06 | 0 | 0 | [5 empty] | QC-12-08896
2012-09-14 | 0 | 0 | [5 empty] | QC-12-09349
2012-09-17 | 0 | 0 | [5 empty] | QC-12-09411
2012-09-28 | 0 | 0 | [5 empty] | QC-12-09815
| 56 |  | 66 | 14 | 0 | 0
RM 140/151/150 | TAMC | Gram Stain/
Date | A1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | [5 empty] | QC-12-06655
2012-07-11 | 0 | [5 empty] | QC-12- 07005
2012-07-19 | 0 | [5 empty] | QC-12-07246
2012-07-27 | 0 | [5 empty] | QC-12-07527
2012-07-30 | 0 | [5 empty] | QC-12-07587 | SDA
2012-08-09 | 3 | 3 |  |  |  |  | QC-12-07889
2012-08-15 | 0 | [5 empty] | QC-12-08051
2012-08-24 | 5 | 5 |  |  |  |  | QC-12-08446
2012-08-30 | 1 | 1 |  |  |  |  | QC-12-08673
2012-09-05 | 5 | 5 |  |  |  |  | QC-12-08848
2012-09-10 | 0 | [5 empty] | QC-12-09046
2012-09-21 | 2 |  | 2 |  |  |  | QC-12-09571
2012-09-24 | 0 | [5 empty] | QC-12-09614
2012-07-02 | 0 | [5 empty] | QC-12-06655
2012-07-11 | 1 | 1 |  |  |  |  | QC-12- 07005
2012-07-19 | 7 |  | 7 |  |  |  | QC-12-07246
2012-07-27 | 0 | [5 empty] | QC-12-07527
2012-07-30 | 0 | [5 empty] | QC-12-07587 | SDA
2012-08-09 | 16 | 16 |  |  |  |  | QC-12-07889
2012-08-15 | 3 |  | 3 |  |  |  | QC-12-08051
2012-08-24 | 22 | 22 |  |  | 1 |  | QC-12-08446 | Mold
2012-08-30 | 0 | [5 empty] | QC-12-08673
2012-09-05 | 14 | 14 |  |  |  |  | QC-12-08848
2012-09-10 | 0 | [5 empty] | QC-12-09046
2012-09-21 | 2 | 1 | 1 |  |  |  | QC-12-09571
2012-09-24 | 2 | 2 |  |  |  |  | QC-12-09614
2012-07-02 | 0 | [5 empty] | QC-12-06655
2012-07-11 | 1 | 1 |  |  |  |  | QC-12- 07005
2012-07-19 | 0 | [5 empty] | QC-12-07246
2012-07-27 | 0 | [5 empty] | QC-12-07527
2012-07-30 | 0 | [5 empty] | QC-12-07587 | SDA
2012-08-09 | 0 | [5 empty] | QC-12-07889
2012-08-15 | 0 | [5 empty] | QC-12-08051
2012-08-24 | 7 | 7 |  |  |  |  | QC-12-08446
2012-08-30 | 5 | 2 | 3 |  |  |  | QC-12-08673
2012-09-05 | 47 | 47 |  |  |  | AL-091312-001 | QC-12-08848
2012-09-10 | 9 | 5 | 4 |  |  |  | QC-12-09046
2012-09-21 | 0 | [5 empty] | QC-12-09571
2012-09-24 | 1 |  | 1 |  |  |  | QC-12-09614
| 39 | 132 | 21 | 0 | 1
RM 141/141L | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | A1 | A2 | A3 | A1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-11 | 25 | 5 | 0 | 0 | 30 |  |  |  |  | QC-12-07005
2012-07-19 | 0 | 0 | 2 | 0 | 1 | 1 |  |  |  | QC-12-07246
2012-07-27 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07527
2012-08-03 | 25 | 4 | 5 | 0 | 19 | 15 |  |  |  | QC-12-07765
2012-08-03 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765 | SDA
2012-08-09 | 3 | 2 | 0 | 0 | 5 |  |  |  |  | QC-12-07889
2012-08-15 | 0 | 0 | 1 | 0 |  | 1 |  |  |  | QC-12-08051
2012-08-24 | 18 | 4 | 8 | 0 | 26 | 4 |  |  |  | QC-12-08446
2012-08-30 | 0 | 1 | 1 | 0 | 2 |  |  |  |  | QC-12-08673
2012-09-05 | 33 | 6 | 20 | 0 | 59 |  |  |  | AL-091312-002 | QC-12-08848
2012-09-10 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09046
2012-09-21 | 0 | 0 | 3 | 0 |  | 3 |  |  |  | QC-12-09571
2012-09-26 | 0 | 0 | 3 | 0 |  | 3 |  |  |  | QC-12-09680
| 56 |  |  |  | 142 | 27 | 0 | 0
RM 160/161 | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | A1 | A1 | A2 | A3 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-09 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06834
2012-07-18 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07207
2012-07-25 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07465
2012-08-01 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07647 | SDA
2012-08-08 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07825
2012-08-17 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08160
2012-08-20 | 2 | 0 | 24 | 1 | 15 | 10 |  | 2 |  | QC-12-08246 | Mold (white, filamentous)
2012-08-31 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08706
2012-09-07 | 1 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-09019
2012-09-14 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09349
2012-09-17 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09411
2012-09-25 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09646
| 52 |  |  |  | 16 | 10 | 0 | 2
RM 162/163/147B | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | A1 | A1 | A2 | A1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-11 | 3 | 0 | 0 | 0 | 3 |  |  |  |  | QC-12- 07005
2012-07-19 | 1 | 1 | 0 | 1 |  | 3 |  |  |  | QC-12-07246
2012-07-27 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07527
2012-08-03 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765 | SDA
2012-08-03 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765
2012-08-09 | 9 | 1 | 0 | 0 | 10 |  |  |  |  | QC-12-07889
2012-08-15 | 1 | 0 | 1 | 0 |  | 2 |  |  |  | QC-12-08051
2012-08-24 | 3 | 3 | 0 | 1 | 7 |  |  |  |  | QC-12-08446
2012-08-30 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08673
2012-09-05 | 1 | 4 | 0 | 0 | 4 | 1 |  |  |  | QC-12-08848
2012-09-10 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09046
2012-09-21 | 0 | 0 | 2 | 1 | 1 | 2 |  |  |  | QC-12-09571
2012-09-26 | 0 | 0 | 2 | 1 | 2 | 1 |  |  |  | QC-12-09680
| 56 |  |  |  | 27 | 9 | 0 | 0
ISO 7
RM 126/127/127L | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | A1 | A1 | A2 | A3 | A1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06807
2012-07-10 | 43 | 2 | 0 | 1 | 0 | 3 |  |  |  | ACT-20120041 | QC-12-06953 | 12-0605, 12-0606
2012-07-11 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07005
2012-07-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07058 | Pre
2012-07-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07058 | Post
2012-07-17 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07169
2012-07-20 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07314
2012-07-24 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07438
2012-07-26 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07511
2012-07-31 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07598 |  |  | 30
2012-08-01 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07647 | SDA |  | 85
2012-08-06 | 1 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-07778
2012-08-08 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07825
2012-08-13 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07957
2012-08-17 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08160
2012-08-20 | 2 | 1 | 1 | 2 | 0 | 6 |  |  |  |  | QC-12-08246
2012-08-22 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08311
2012-08-31 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08706
2012-09-04 | 0 | 0 | 0 | 2 | 0 | 1 |  | 1 |  |  | QC-12-08819
2012-09-07 | 1 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-09019
2012-09-12 | 1 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-09195
2012-09-14 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09349
2012-09-17 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09411
2012-09-18 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09457
2012-09-24 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09614
2012-09-25 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09646
| 135 |  |  |  |  | 12 | 1 | 1 | 0
RM 130/131/131L | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | A1 | A1 | A2 | A3 | A1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-05 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06765
2012-07-09 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06834
2012-07-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07045
2012-07-18 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07207
2012-07-20 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07314
2012-07-25 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07465
2012-07-26 | 0 | 0 | 2 | 0 | 0 | 1 | 1 |  |  |  | QC-12-07511
2012-07-30 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07587 | SDA
2012-07-31 | 0 | 0 | 0 | 1 | 0 |  |  |  | 1 |  | QC-12-07598 | Mold: small, raised, green, crate foam
2012-08-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07778
2012-08-07 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07802
2012-08-13 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07957
2012-08-14 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08007
2012-08-21 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08259
2012-08-22 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08311
2012-08-28 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08570
2012-08-29 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08628
2012-09-04 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08819
2012-09-07 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09019
2012-09-11 | 0 | 0 | 1 | 4 | 0 | 5 |  |  |  |  | QC-12-09154
2012-09-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09195
2012-09-17 | 1 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-09411
2012-09-19 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09485
2012-09-20 | 0 | 1 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-09544
2012-09-24 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09614
2012-09-25 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09646
| 135 |  |  |  |  | 7 | 2 | 0 | 1
RM 132/133/133L | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | A1 | A1 | A2 | A3 | A1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-05 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06765
2012-07-09 | 0 | 1 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-06834
2012-07-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07045
2012-07-18 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07207
2012-07-20 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07314
2012-07-25 | 1 | 0 | 0 | 0 | 0 |  |  | 1 |  |  | QC-12-07465
2012-07-26 | 1 | 0 | 0 | 1 | 0 | 2 |  |  |  |  | QC-12-07511
2012-07-30 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07587 | SDA
2012-07-31 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07598
2012-08-07 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07802
2012-08-10 | 0 | 4 | 23 | 5 | 0 | 9 |  |  |  | ACT-20120055 | QC-12-07898 | 12-0666 to 12-0671
2012-08-14 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08007
2012-08-16 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08106
2012-08-21 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08259
2012-08-23 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08410
2012-08-27 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08532
2012-08-28 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08570
2012-08-29 | 0 | 0 | 2 | 0 | 0 | [5 empty] | QC-12-08628
2012-09-04 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08819
2012-09-06 | 2 | 0 | 0 | 0 | 0 |  | 2 |  |  |  | QC-12-08896
2012-09-11 | 0 | 0 | 1 | 0 | 0 | 1 |  |  |  |  | QC-12-09154
2012-09-13 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09221
2012-09-17 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09411
2012-09-20 | 0 | 1 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-09544
2012-09-25 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09746
2012-09-27 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09646
| 135 |  |  |  |  | 13 | 3 | 1 | 0
RM 152/156 | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | A1 | A1 | A2 | A3 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-06 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06807
2012-07-09 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06834
2012-07-13 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07108
2012-07-16 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07130
2012-07-18 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07207
2012-07-23 | 2 | 0 | 0 | 0 | 2 |  |  |  |  | QC-12-07396
2012-07-25 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07465
2012-08-01 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07647 | SDA
2012-08-02 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07737
2012-08-07 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07802
2012-08-10 | 1 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-07898
2012-08-14 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08007
2012-08-16 | 7 | 0 | 0 | 0 | 7 |  |  |  | AL-090712-001 | QC-12-08106
2012-08-21 | 1 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-08259
2012-08-23 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08410
2012-08-27 | 1 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-08532
2012-08-28 | 1 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-08570
2012-08-29 | 3 | 0 | 0 | 0 | 3 |  |  |  |  | QC-12-08628
2012-09-04 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08819
2012-09-07 | 1 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-09019
2012-09-11 | 2 | 0 | 0 | 2 | 4 |  |  |  |  | QC-12-09154
2012-09-13 | 1 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-09221
2012-09-17 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09411
2012-09-20 | 1 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-09544
2012-09-27 | 4 | 0 | 0 | 0 | 4 |  |  |  |  | QC-12-09746
2012-09-28 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09815
| 108 |  |  |  | 25 | 2 | 0 | 0
RM 154/153/153L | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | A1 | A1 | A2 | A3 | A1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06807
2012-07-10 | 14 | 0 | 0 | 0 | 0 |  |  |  |  | ACT-20120040 | QC-12-06953 | 12-0605, 12-0606, 12-0607
2012-07-13 | 1 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-07108
2012-07-16 | 1 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-07130
2012-07-17 | 1 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-07169
2012-07-23 | 5 | 0 | 0 | 0 | 0 | 5 |  |  |  |  | QC-12-07396
2012-07-24 | 0 | 0 | 1 | 0 | 0 | 1 |  |  |  |  | QC-12-07438
2012-08-01 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07647 | SDA
2012-08-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07737
2012-08-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07778
2012-08-07 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07802
2012-08-13 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07957
2012-08-14 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08007
2012-08-22 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08311
2012-08-23 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08410
2012-08-28 | 1 | 1 | 0 | 0 | 0 | 1 |  |  | 1 |  | QC-12-08570
2012-08-29 | 1 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-08628
2012-08-30 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08673
2012-08-31 |  | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08706
2012-09-04 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08819
2012-09-07 | 1 | 0 | 0 | 1 | 0 | 1 |  |  | 1 |  | QC-12-09019 | Yeast
2012-09-11 | 10 | 0 | 0 | 0 | 0 | 10 |  |  |  |  | QC-12-09154
2012-09-12 | 0 | 28 | 93 | 26 | 0 |  |  |  |  | ACT-20120079 | QC-12-09195 | 12-0787,12-0788,12-0789,12-0790,12-0785,12-0786
2012-09-14 | 0 | 1 | 0 | 0 | 0 |  |  |  | 1 |  | QC-12-09349 | Yeast
2012-09-17 | 1 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-09411
2012-09-20 | 0 | 1 | 1 | 0 | 0 | 1 | 1 |  |  |  | QC-12-09544
2012-09-27 | 1 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-09746
2012-09-28 | 0 | 0 | 1 | 0 | 0 |  | 1 |  |  |  | QC-12-09815
| 144 |  |  |  |  | 22 | 5 | 0 | 3
RM 157/158/159 | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | A1 | A1 | A1 | A2 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-03 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06750
2012-07-11 | 0 | 1 | 0 | 1 | 2 |  |  |  |  | QC-12- 07005
2012-07-13 | 2 | 0 | 1 | 0 |  | 3 |  |  |  | QC-12-07108
2012-07-16 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07130
2012-07-19 | 0 | 1 | 0 | 0 |  | 1 |  |  |  | QC-12-07246
2012-07-23 | 0 | 1 | 0 | 0 | 1 |  |  |  |  | QC-12-07396
2012-07-27 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07527
2012-08-02 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07737
2012-08-03 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765 | SDA
2012-08-03 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765
2012-08-09 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07889
2012-08-10 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07898
2012-08-15 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08051
2012-08-23 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08410
| 60 |  |  |  | 3 | 4 | 0 | 0
Aseptic Core
RM 143/144/145 | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | A1 | A2 | A1 | A2 | A3 | A1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-03 | 1 | 0 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-06696
2012-07-10 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06909
2012-07-13 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07113
2012-07-16 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07122
2012-07-18 | 0 | 0 | 1 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-07194
2012-07-23 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07398
2012-07-25 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07466
2012-07-31 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07628 | SDA
2012-07-31 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07627
2012-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07674
2012-08-07 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07809
2012-08-09 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07894
2012-08-13 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07961
2012-08-16 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08084
2012-08-23 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08416
2012-08-24 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08482
2012-08-28 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08548
2012-08-30 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08683
2012-09-04 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08821
2012-09-05 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08854
2012-09-10 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09062
2012-09-11 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09120
2012-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09448
2012-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09573
2012-09-24 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09631
2012-09-26 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09682
| 162 | [5 empty] | 1 | 1 | 0 | 0

## SV
ISO 8
RM 119/138/139 | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | S1 | S2 | S3 | S4 | F1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-12 | 0 | 1 | 0 | 0 | 1 |  | 2 |  |  |  | QC-12-07045
2012-07-20 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07314
2012-07-24 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07438 |  |  | 119 S | 119 F | 138 S | 138 F | 140 S | 140 F
2012-07-30 | 0 | 1 | 0 | 0 | 0 |  |  |  | 1 |  | QC-12-07587 | Mold (white) SDA |  | 0.16667 | 0.16667 | 0.0625 | 0.41667 | 0 | 0.84615
2012-08-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07778
2012-08-13 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07957
2012-08-22 | 0 | 0 | 0 | 0 | 1 |  |  | 1 |  |  | QC-12-08311
2012-09-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08896
2012-09-12 | 3 | 0 | 0 | 0 | 0 | 2 |  |  | 1 |  | QC-12-09195 | Yeast
2012-09-19 | 0 | 1 | 1 | 0 | 0 | 2 |  |  |  |  | QC-12-09485
2012-09-24 | 0 | 1 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-09614 | GPR w/spores
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-12 | 0 | 0 | 1 | 0 | 0 |  | 1 |  |  |  | QC-12-07045
2012-07-20 | 0 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12-07314
2012-07-26 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07511
2012-07-30 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07587 | SDA
2012-08-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07778
2012-08-13 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07957
2012-08-22 | 0 | 0 | 1 | 0 | 1 | 1 | 1 |  |  |  | QC-12-08311
2012-09-06 | 0 | 0 | 0 | 0 | 1 |  |  |  | 1 |  | QC-12-08896 | Mold (white)
2012-09-12 | 0 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12-09195
2012-09-19 | 1 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12-09485 | 12-0838
2012-09-24 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09614
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07045
2012-07-20 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07314
2012-07-26 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07511
2012-07-30 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07587 | SDA
2012-08-06 | 0 | 0 | 0 | 0 | 2 |  | 2 |  |  |  | QC-12-07778
2012-08-13 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07957
2012-08-22 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08311
2012-09-06 | 0 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12-08896
2012-09-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09195
2012-09-19 | 0 | 0 | 0 | 3 | 0 | 3 |  |  |  |  | QC-12-09485
2012-09-24 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  | QC-12-09614 | GPR w/spores
| 180 |  |  |  |  | 12 | 8 | 1 | 3
RM 128/129/129L | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | S1 | S2 | S3 | S4 | F1 | GPC | GPR | GNR | GVR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-06655
2012-07-13 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07108
2012-07-16 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | QC-12-07130
2012-07-23 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07396
2012-08-02 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07737
2012-08-03 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07738 | SDA
2012-08-10 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | QC-12-07898
2012-08-16 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | QC-12-08106
2012-08-21 | 0 | 0 | 0 | 0 | 2 | 2 | [5 empty] | QC-12-08259
2012-08-27 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08532
2012-09-06 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08896
2012-09-13 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-09221
2012-09-17 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  |  | QC-12-09411
2012-09-28 | 0 | 0 | 0 | 0 | 2 | 2 | [5 empty] | QC-12-09815
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-06655
2012-07-13 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07108
2012-07-16 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07130
2012-07-23 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07396
2012-08-02 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07737
2012-08-03 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07738 | SDA
2012-08-10 | 1 | 1 | 0 | 0 | 4 | 3 | 3 |  |  |  |  | QC-12-07898
2012-08-16 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08106
2012-08-21 | 0 | 0 | 0 | 1 | 0 |  | 1 |  |  |  |  | QC-12-08259 | W/spores
2012-08-27 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08532
2012-09-06 | 0 | 0 | 0 | 0 | 2 |  | 2 |  |  |  |  | QC-12-08896
2012-09-13 | 1 | 0 | 0 | 0 | 1 | 1 | 1 |  |  |  |  | QC-12-09221
2012-09-17 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  |  | QC-12-09411
2012-09-28 | 0 | 0 | 0 | 0 | 5 | 1 |  |  |  | 4 |  | QC-12-09815 | 12-0867, 12-0868
2012-07-02 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-06655
2012-07-13 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-07108
2012-07-16 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-07130
2012-07-23 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-07396
2012-08-02 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-07737
2012-08-03 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-07738 | SDA
2012-08-10 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-07898
2012-08-16 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-08106
2012-08-21 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-08259
2012-08-27 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-08532
2012-09-06 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-08896
2012-09-13 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-09221
2012-09-17 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-09411
2012-09-28 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-09815
| 196 | 182 |  |  |  | 12 | 9 | 0 | 0 | 4
RM 134/135/135L | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | S1 | S2 | S3 | S4 | F1 | GPC | GPR | GNR | GVR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-06655
2012-07-10 | 0 | 0 | 0 | 0 | 5 |  | 5 |  |  |  |  | QC-12-06953
2012-07-17 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07169
2012-07-24 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07438
2012-07-30 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07587 | SDA
2012-08-08 | 0 | 0 | 0 | 0 | 2 |  | 2 |  |  |  |  | QC-12-07825
2012-08-17 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08160
2012-08-20 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  |  | QC-12-08246 | W/spores
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-06655
2012-07-10 | 1 | 0 | 0 | 0 | 2 |  | 3 |  |  |  |  | QC-12-06953
2012-07-17 | 2 | 0 | 0 | 0 | 1 | 1 |  |  |  | 2 |  | QC-12-07169 | Small, white, mold
2012-07-24 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07438
2012-07-30 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07587 | SDA
2012-08-08 | 2 | 0 | 0 | 0 | 1 |  | 3 |  |  |  |  | QC-12-07825
2012-08-17 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08160
2012-08-20 | 3 | 0 | 0 | 0 | 4 | 3 | 4 |  |  |  |  | QC-12-08246
2012-07-02 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-06655
2012-07-10 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-06953
2012-07-17 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-07169
2012-07-24 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-07438
2012-07-30 | 0 | 0 | 0 | 0 | [7 empty] | QC-12-07587 | SDA
| 100 |  |  |  |  | 4 | 18 | 0 | 0 | 2
RM 136/137 | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | S1 | S2 | S3 | S4 | F1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-10 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06953
2012-07-17 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  | QC-12-07169
2012-07-24 | 1 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-07438
2012-07-31 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07598
2012-07-31 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07599 | SDA
2012-08-08 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07825
2012-08-17 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08160
2012-08-20 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08246
2012-08-31 | 2 | 0 | 0 | 0 | 0 | 2 |  |  |  |  | QC-12-08706
2012-09-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08896
2012-09-14 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09349
2012-09-17 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09411
2012-09-20 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08246
2012-09-28 | 1 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-09815
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-10 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06953
2012-07-17 | 0 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12-07169
2012-07-24 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07438
2012-07-31 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07598
2012-07-31 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07599 | SDA
2012-08-08 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07825
2012-08-17 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08160
2012-08-20 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  | QC-12-08246
2012-08-31 | 0 | 3 | 0 | 0 | 1 | 3 | 1 |  |  |  | QC-12-08706
2012-09-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08896
2012-09-14 | 0 | 0 | 0 | 0 | 4 | 3 | 1 |  |  |  | QC-12-09349
2012-09-17 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09411
2012-09-20 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  | QC-12-08246 | GPR w / spores
2012-09-28 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  | QC-12-09815 | Spreader, GPR w/spores
| 150 |  |  |  |  | 10 | 7 | 0 | 0
RM 140/151/150 | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | S1 | S2 | S3 | S4 | F1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-11 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12- 07005
2012-07-19 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07246
2012-07-27 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07527
2012-07-30 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07587 | SDA
2012-08-09 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  | QC-12-07889 | w/spores
2012-08-15 | 0 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12-08051
2012-08-24 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08446
2012-08-30 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08673
2012-09-05 | 0 | 0 | 0 | 0 | 7 |  |  | 7 |  |  | QC-12-08848
2012-09-10 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09046
2012-09-21 | 0 | 0 | 0 | 0 | 2 |  |  |  | 2 |  | QC-12-09571 | 12-0842
2012-09-24 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09614
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-11 | 0 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12- 07005
2012-07-19 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07246
2012-07-27 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07527
2012-07-30 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07587 | SDA
2012-08-09 | 0 | 0 | 11 | 0 | 2 | 11 | 2 |  |  |  | QC-12-07889
2012-08-15 | 0 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12-08051
2012-08-24 | 0 | 0 | 0 | 0 | 5 | 5 |  |  |  |  | QC-12-08446
2012-08-30 | 0 | 0 | 0 | 2 | 0 | 2 |  |  |  |  | QC-12-08673
2012-09-05 | 0 | 0 | 6 | 0 | 1 | 1 |  |  | 6 |  | QC-12-08848 | Mold (white, large, filamentous
2012-09-10 | 0 | 1 | 5 | 0 | 0 | 3 | 2 |  | 1 |  | QC-12-09046 | Mold (White)
2012-09-21 | 0 | 0 | 0 | 0 | 6 | 3 | 2 | 1 |  |  | QC-12-09571
2012-09-24 | 0 | 0 | 0 | 2 | 1 | 1 | 2 |  |  |  | QC-12-09614 | GPR w/spores
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-11 | 1 | 0 | 0 | 0 | 7 | 8 |  |  |  |  | QC-12- 07005
2012-07-19 | 0 | 0 | 0 | 0 | 2 |  | 2 |  |  |  | QC-12-07246 | W/ spores
2012-07-27 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07527
2012-07-30 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07587 | SDA
2012-08-09 | 0 | 0 | 2 | 7 | 1 | 9 | 1 |  | 1 |  | QC-12-07889 | mold (black, small, filamentous
2012-08-15 | 1 | 0 | 1 | 0 | 3 | 3 | 1 |  | 1 |  | QC-12-08051 | Large, pink mold
2012-08-24 | 0 | 0 | 0 | 4 | 4 | 4 | 4 |  |  |  | QC-12-08446
2012-08-30 | 1 | 0 | 0 | 0 | 1 | 2 |  |  |  |  | QC-12-08673
2012-09-05 | 1 | 0 | 0 | 0 | 6 |  | 7 |  |  |  | QC-12-08848
2012-09-10 | 1 | 0 | 0 | 6 | 0 | 5 |  |  | 2 |  | QC-12-09046 | Mold (White)
2012-09-21 | 0 | 0 | 0 | 0 | 4 | 2 |  | 2 |  |  | QC-12-09571
2012-09-24 | 0 | 0 | 0 | 0 | 3 | 2 |  |  | 1 |  | QC-12-09614
| 195 |  |  |  |  | 64 | 24 | 10 | 14
RM 141/141L | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | S1 | S2 | S3 | S4 | S5 | F1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  | QC-12-06655
2012-07-11 | 3 | 0 | 0 | 0 | 0 | 6 | 3 | 3 |  | 3 |  | QC-12-07005 | Mold: Large, White; GPR
2012-07-19 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07246
2012-07-27 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07527
2012-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765 | SDA
2012-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765
2012-08-09 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07889
2012-08-15 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08051
2012-08-24 | 0 | 2 | 0 | 0 | 0 | 0 | 2 |  |  |  |  | QC-12-08446
2012-08-30 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08673
2012-09-05 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08848
2012-09-10 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09046
2012-09-21 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  | QC-12-09571
2012-09-26 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12-09680
2012-07-02 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-11 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07005
2012-07-19 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07246
2012-07-27 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07527
2012-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765 | SDA
2012-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765
2012-08-09 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07889
2012-08-15 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08051
2012-08-24 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08446
2012-08-30 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08673
2012-09-05 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08848
2012-09-10 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09046
2012-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09571
2012-09-26 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09680
| S1: 112 | 6 | 5 | 0 | 3
RM 160/161 | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | S1 | S2 | S3 | S4 | S5 | S6 | S7 | F1 | F2 | F3 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 1 |  | QC-12-06655 | Mold (White)
2012-07-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06834
2012-07-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07207
2012-07-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07465
2012-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07647 | SDA
2012-08-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07825
2012-08-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08160
2012-08-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 |  |  |  |  | QC-12-08246
2012-08-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08706
2012-09-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09019
2012-09-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09349
2012-09-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09411
2012-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09646
2012-07-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06834
2012-07-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 2 |  | 1 |  | QC-12-07207 | Small, white
2012-07-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 |  |  |  |  | QC-12-07465
2012-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07647 | SDA
2012-08-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  |  |  | 1 |  | QC-12-07825 | Mold(white)
2012-08-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08160
2012-08-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 1 | 5 | 1 |  |  |  | QC-12-08246
2012-08-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08706
2012-09-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09019
2012-09-14 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 1 | 1 | 0 |  | 4 | 1 | 2 |  | QC-12-09349 | GPR w/spores. 12-0802, 12-0803
2012-09-17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 2 |  |  |  | QC-12-09411
2012-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09646
| S1: 195 | 8 | 9 | 1 | 5
RM 162/163/147B | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | S1 | S2 | S3 | S4 | S5 | S6 | F1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-11 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 |  |  |  |  | QC-12- 07005
2012-07-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07246
2012-07-27 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  |  |  |  | QC-12-07527
2012-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765 | SDA
2012-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765
2012-08-09 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 7 |  |  |  |  | QC-12-07889
2012-08-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08051
2012-08-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08446
2012-08-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08673
2012-09-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08848
2012-09-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09046
2012-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09571
2012-09-26 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  | QC-12-09680
2012-07-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12- 07005
2012-07-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07246
2012-07-27 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 6 |  |  |  |  | QC-12-07527
2012-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765 | SDA
2012-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765
2012-08-09 | 1 | 0 | 0 | 0 | 0 | 11 | 1 | 13 |  |  |  |  | QC-12-07889
2012-08-15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-08051
2012-08-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08446
2012-08-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08673
2012-09-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08848
2012-09-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09046
2012-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12-09571
2012-09-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09680
2012-07-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12- 07005
2012-07-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07246
2012-07-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07527
2012-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765 | SDA
2012-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765
2012-08-09 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | [5 empty] | QC-12-07889
2012-08-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08051
2012-08-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08446
2012-08-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08673
2012-09-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08848
2012-09-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09046
2012-09-21 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2 |  |  |  |  | QC-12-09571
2012-09-26 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 |  |  |  |  | QC-12-09680
| S1: 238 | 40 | 1 | 0 | 0
ISO 7
RM 126/127/127L | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | S1 | S2 | S3 | S4 | F1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06807
2012-07-10 | 0 | 0 | 0 | 0 | 2 | 2 |  |  |  |  | QC-12-06953
2012-07-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07058 | Pre
2012-07-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07058 | Post
2012-07-17 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07169
2012-07-20 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07314
2012-07-24 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07438
2012-07-26 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07511
2012-07-31 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07598
2012-08-01 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07647
2012-08-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07778
2012-08-08 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07825
2012-08-13 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07957
2012-08-17 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08160
2012-08-20 | 0 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12-08246
2012-08-22 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08311
2012-08-31 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08706
2012-09-04 | 0 | 1 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-08819
2012-09-07 | 0 | 0 | 0 | 0 | 3 |  | 3 |  |  |  | QC-12-09019
2012-09-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09195
2012-09-14 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09349
2012-09-17 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09411
2012-09-18 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09457
2012-09-24 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09614
2012-09-25 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09646
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06807
2012-07-10 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06953
2012-07-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07058 | Pre
2012-07-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07058 | Post
2012-07-17 | 10 | 0 | 0 | 0 | 0 |  |  |  |  | ACT-20120042 | QC-12-07169 | 12-0616
2012-07-20 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07314
2012-07-24 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07438
2012-07-26 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07511
2012-07-31 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07598
2012-08-01 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07647 | SDA
2012-08-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07778
2012-08-08 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07825
2012-08-13 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07957
2012-08-17 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08160
2012-08-20 | 0 | 0 | 1 | 0 | 0 |  | 1 |  |  |  | QC-12-08246
2012-08-22 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08311
2012-08-31 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08706
2012-09-04 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08819
2012-09-07 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09019
2012-09-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09195
2012-09-14 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09349
2012-09-17 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09411
2012-09-18 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09457
2012-09-24 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09614
2012-09-25 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09646
2012-07-02 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-06655
2012-07-06 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-06807
2012-07-10 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-06953
2012-07-11 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12- 07005
2012-07-12 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07058 | Pre
2012-07-12 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07058 | Post
2012-07-17 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07169
2012-07-20 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07314
2012-07-24 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07438
2012-07-26 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07511
2012-07-31 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07598
2012-08-01 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07647 | SDA
2012-08-06 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07778
2012-08-08 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07825
2012-08-13 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07957
2012-08-17 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-08160
2012-08-20 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-08246
2012-08-22 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-08311
2012-08-31 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-08706
2012-09-04 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-08819
2012-09-07 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-09019
2012-09-12 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-09195
2012-09-14 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-09349
2012-09-17 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-09411
2012-09-18 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-09457
2012-09-24 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-09614
2012-09-25 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-09646
| S1: 368; S6: 4; F1: 4 | 0 | 0
RM 130/131/131L | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | S1 | S2 | S3 | S4 | F1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-05 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06765
2012-07-09 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06834
2012-07-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07045
2012-07-18 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07207
2012-07-20 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07314
2012-07-25 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07465
2012-07-26 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07511
2012-07-30 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07587 | SDA
2012-07-31 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07598
2012-08-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07778
2012-08-07 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07802
2012-08-13 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07957
2012-08-14 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08007
2012-08-21 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08259
2012-08-22 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08311
2012-08-28 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08570
2012-08-29 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08628
2012-09-04 | 0 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12-08819
2012-09-07 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09019
2012-09-11 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09154
2012-09-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09195
2012-09-17 | 0 | 1 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-09411
2012-09-19 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09485
2012-09-20 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09544
2012-09-24 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09614
2012-09-25 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09646
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-05 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06765
2012-07-09 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06834
2012-07-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07045
2012-07-18 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07207
2012-07-20 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07314
2012-07-25 | 0 | 0 | 1 | 0 | 0 |  |  |  | 1 |  | QC-12-07465 | Small, white mold
2012-07-26 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07511
2012-07-30 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07587 | SDA
2012-07-31 | 3 | 13 | 0 | 1 | 2 |  |  |  | 19 | ACT-20120052 | QC-12-07598 | 12-0650
2012-08-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07778
2012-08-07 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07802
2012-08-13 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07957
2012-08-14 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08007
2012-08-21 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08259
2012-08-22 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08311
2012-08-28 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08570
2012-08-29 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08628
2012-09-04 | 0 | 1 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-08819
2012-09-07 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09019
2012-09-11 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09154
2012-09-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09195
2012-09-17 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09411
2012-09-19 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09485
2012-09-20 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09544
2012-09-24 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09614
2012-09-25 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09646
2012-07-02 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-06655
2012-07-05 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-06765
2012-07-09 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-06834
2012-07-12 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-07045
2012-07-18 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-07207
2012-07-20 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-07314
2012-07-25 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-07465
2012-07-26 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-07511
2012-07-30 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-07587 | SDA
2012-07-31 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-07598
2012-08-06 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-07778
2012-08-07 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-07802
2012-08-13 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-07957
2012-08-14 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-08007
2012-08-21 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-08259
2012-08-22 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-08311
2012-08-28 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-08570
2012-08-29 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-08628
2012-09-04 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-08819
2012-09-07 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-09019
2012-09-11 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-09154
2012-09-12 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-09195
2012-09-17 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-09411
2012-09-19 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-09485
2012-09-20 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-09544
2012-09-24 | S1: 0; S2: 1; S3: 0 |  |  | ACT-20120084 | QC-12-09614 | 12-843
2012-09-25 | S1: 0; S2: 0; S3: 0 |  |  |  | QC-12-09646
| S1: 351; S6: 3; F1: 0 | 0 | 20
RM 132/133/133L | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | S1 | S2 | S3 | S4 | F1 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-05 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06765
2012-07-09 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06834
2012-07-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07045
2012-07-18 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07207
2012-07-20 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07314
2012-07-25 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07465
2012-07-26 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07511
2012-07-30 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07587 | SDA
2012-07-31 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07598
2012-08-07 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07802
2012-08-10 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07898
2012-08-14 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08007
2012-08-16 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08106
2012-08-21 | 0 | 1 | 0 | 0 | 2 | 2 |  |  | 1 |  | QC-12-08259 | medium, white
2012-08-23 | 0 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12-08410
2012-08-27 | 0 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12-08532
2012-08-28 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08570
2012-08-29 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08628
2012-09-04 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08819
2012-09-06 | 0 | 1 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-08896
2012-09-11 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09154
2012-09-13 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  | QC-12-09221
2012-09-17 | 0 | 1 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-09411
2012-09-20 | 0 | 1 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-09544
2012-09-25 | 0 | 1 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-09646
2012-09-27 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09746
2012-07-02 | 0 | 0 | 1 | 0 | 0 |  |  |  | 1 |  | QC-12-06655 | Mold (white)
2012-07-05 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06765
2012-07-09 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06834
2012-07-12 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07045
2012-07-18 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07207
2012-07-20 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07314
2012-07-25 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  | QC-12-07465 | w/spores
2012-07-26 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07511
2012-07-30 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07587 | SDA
2012-07-31 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07598
2012-08-07 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07802
2012-08-10 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07898
2012-08-14 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08007
2012-08-16 | 1 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-08106 | GPR w/spores
2012-08-21 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08259
2012-08-23 | 0 | 0 | 1 | 0 | 0 |  | 1 |  |  |  | QC-12-08410
2012-08-27 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  | QC-12-08532 | GPR w/spores
2012-08-28 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08570
2012-08-29 | 0 | 2 | 1 | 0 | 0 | 1 |  | 1 |  |  | QC-12-08628 | GPR w/spores
2012-09-04 | 0 | 0 | 0 | 0 | 1 |  |  | 1 |  |  | QC-12-08819
2012-09-06 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08896
2012-09-11 | 1 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | QC-12-09154
2012-09-13 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09221
2012-09-17 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09411
2012-09-20 | 1 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-09544
2012-09-25 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09646
2012-09-27 | 1 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-09746
2012-07-02 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-06655
2012-07-05 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-06765
2012-07-09 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-06834
2012-07-12 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07045
2012-07-18 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07207
2012-07-20 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07314
2012-07-25 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07465
2012-07-26 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07511
2012-07-30 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07587 | SDA
2012-07-31 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07598
2012-08-07 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07802
2012-08-10 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-07898
2012-08-14 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-08007
2012-08-16 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-08106
2012-08-21 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-08259
2012-08-23 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-08410
2012-08-27 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-08532
2012-08-28 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-08570
2012-08-29 | S1: 1; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-08628
2012-09-04 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-08819
2012-09-06 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-08896
2012-09-11 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-09154
2012-09-13 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-09221
2012-09-17 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-09411
2012-09-20 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-09544
2012-09-25 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-09646
2012-09-27 | S1: 0; S2: 0; S3: 0; S4: 0 |  |  |  | QC-12-09746
| S1: 378; S6: 9; F1: 8 | 2 | 2
RM 152/156 | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | S1 | S2 | S3 | S4 | S5 | S6 | F1 | F2 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06807
2012-07-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06834
2012-07-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07108
2012-07-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07130
2012-07-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07207
2012-07-23 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 |  |  |  | QC-12-07396
2012-07-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07465
2012-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07647 | SDA
2012-08-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07737
2012-08-07 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 |  |  |  | QC-12-07802
2012-08-10 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-07898
2012-08-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08007
2012-08-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08106
2012-08-21 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 |  |  |  | QC-12-08259
2012-08-23 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  | 1 |  | QC-12-08410 | Convex, small, white mold
2012-08-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08532
2012-08-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08570
2012-08-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08628
2012-09-04 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-08819
2012-09-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09019
2012-09-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09154
2012-09-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09221
2012-09-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09411
2012-09-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09544
2012-09-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09746
2012-09-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09815
2012-07-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06807
2012-07-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06834
2012-07-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07108
2012-07-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07130
2012-07-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  |  | 2 |  |  | QC-12-07207
2012-07-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07396
2012-07-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07465
2012-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07647
2012-08-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07737
2012-08-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  | QC-12-07802 | w/spores
2012-08-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  |  | 1 |  | QC-12-07898 | Small, white mold
2012-08-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08007
2012-08-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08106
2012-08-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  | QC-12-08259 | W/Spores
2012-08-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  |  |  | 1 |  | QC-12-08410 | Convex, small, white mold
2012-08-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 |  |  |  | QC-12-08532 | w/spores
2012-08-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08570
2012-08-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08628
2012-09-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08819
2012-09-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09019
2012-09-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09154
2012-09-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09221
2012-09-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09411
2012-09-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09544
2012-09-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09746
2012-09-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09815
| S1: 351 | 0 | 10 | 2 | 3
RM 154/153/153L | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | S1 | S2 | S3 | S4 | S5 | S6 | S7 | F1 | F2 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-06655
2012-07-06 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-06807
2012-07-10 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 1 | [5 empty] | QC-12-06953
2012-07-13 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-07108
2012-07-16 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-07130
2012-07-17 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-07169
2012-07-23 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 1 |  | 1 |  |  |  | QC-12-07396 | GPR w/spores
2012-07-24 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 2 | 1 | 1 |  |  |  | QC-12-07438
2012-08-01 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-07647 | SDA
2012-08-02 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-07737
2012-08-06 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-07778
2012-08-07 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-07802
2012-08-13 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-07957
2012-08-14 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-08007
2012-08-22 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 2 |  |  |  | 2 |  | QC-12-08311 | Large white/ small white mold
2012-08-23 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 3 | 1 |  |  | 2 |  | QC-12-08410 | Mold: large tan crateform; white raised small
2012-08-28 | S1: 1; S2: 0; S3: 0; S4: 0; F1: 12 | 1 |  |  |  | ACT-20120067 | QC-12-08570 | 12-0731 to 12-0737
2012-08-29 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 1 | 1 |  |  |  |  | QC-12-08628
2012-08-30 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 3 | 2 | 1 |  |  |  | QC-12-08673
2012-09-04 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-08819
2012-09-07 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-09019
2012-09-11 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 3 | 3
2012-09-12 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 2 | 2 |  |  |  |  | QC-12-09195
2012-09-14 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-09349
2012-09-17 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-09411
2012-09-20 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-09544
2012-09-27 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-09746
2012-09-28 | S1: 0; S2: 0; S3: 0; S4: 0; F1: 0 | [5 empty] | QC-12-09815
2012-07-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06807
2012-07-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  |  |  |  | QC-12-06953
2012-07-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07108
2012-07-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07130
2012-07-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07169
2012-07-23 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2 |  | QC-12-07396 | yeast (pink, round, convex)
2012-07-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07438
2012-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07647 | SDA
2012-08-02 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 |  |  |  | QC-12-07737 | Yeast ,GPR w/spores
2012-08-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07778
2012-08-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07802
2012-08-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07957
2012-08-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08007
2012-08-22 | 0 | 0 | 22 | 0 | 0 | 0 | 1 | 0 | 1 | 1 |  |  | 1 | ACT-20120063 | QC-12-08311 | 12-0698,12-0699 medium, white mold
2012-08-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08410
2012-08-28 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 |  |  | 2 |  | QC-12-08570
2012-08-29 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | ACT-20120071 | QC-12-08628 | 12-0754, 12-0755
2012-08-30 | 0 | 0 | 79 | 0 | 1 | 0 | 0 | 0 | 0 |  | 1 |  | 79 | ACT-20120070 | QC-12-08673 | 12-0750 to 12-0753. GPR w/spores
2012-08-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08706
2012-09-04 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 1 |  | QC-12-08819 | White mold
2012-09-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09019
2012-09-11 | 1 | 150 |  | 0 | 0 | 0 | 1 | 0 | 2 | 2 | 1 |  | 1 | ACT-20120077 | QC-12-09154 | GPR w/spores, mold (white, round), 12-0880
2012-09-12 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 |  |  |  | QC-12-09195 | 12-0784. GPR w/spores
2012-09-14 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09349 | 12-09349
2012-09-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09411
2012-09-20 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 |  |  |  | QC-12-09544
2012-09-27 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | AL-100912-002 | QC-12-09746 | 12-0888
2012-09-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09815
2012-07-02 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-06655
2012-07-06 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-06807
2012-07-10 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-06953
2012-07-13 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-07108
2012-07-16 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-07130
2012-07-17 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-07169
2012-07-23 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-07396
2012-07-24 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-07438
2012-08-01 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-07647 | SDA
2012-08-03 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-07737
2012-08-06 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-07778
2012-08-07 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-07802
2012-08-13 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-07957
2012-08-14 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-08007
2012-08-22 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-08311
2012-08-23 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-08410
2012-08-28 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-08570
2012-08-29 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-08628
2012-08-30 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-08673
2012-08-31 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-08706
2012-09-04 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-08819
2012-09-07 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-09019
2012-09-12 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-09195
2012-09-14 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-09349
2012-09-17 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-09411
2012-09-20 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-09544
2012-09-27 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-09746
2012-09-28 | S1: 0; S2: 0; S3: 0 | [5 empty] | QC-12-09815
| S1: 484 | 16 | 9 | 0 | 90
RM 157/158/159 | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | S1 | S2 | S3 | S4 | S5 | S6 | F1 | F2 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-06655
2012-07-03 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-06750
2012-07-11 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12- 07005
2012-07-13 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07108
2012-07-16 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07130
2012-07-19 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07246
2012-07-23 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07396
2012-07-27 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07527
2012-08-02 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07737
2012-08-03 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07765 | SDA
2012-08-03 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07765
2012-08-09 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07889
2012-08-10 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07898
2012-08-15 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08051
2012-08-23 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08410
2012-07-02 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-06655
2012-07-03 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-06750
2012-07-11 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12- 07005
2012-07-13 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07108
2012-07-16 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07130
2012-07-19 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07246
2012-07-23 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07396
2012-07-27 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07527
2012-08-02 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07737
2012-08-03 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07765 | SDA
2012-08-03 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07765
2012-08-09 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07889
2012-08-10 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07898
2012-08-15 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08051
2012-08-23 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08410
2012-07-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06750
2012-07-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12- 07005
2012-07-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07108
2012-07-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07130
2012-07-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  |  |  |  | QC-12-07246
2012-07-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07396
2012-07-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07527
2012-08-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07737
2012-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765 | SDA
2012-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07765
2012-08-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07889
2012-08-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07898
2012-08-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08051
2012-08-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08410
| S1: 270 | 1 | 0 | 0 | 0
Extra Samples |  | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | Room | #1 | #2 | #3 | #4 | #5 | GPC | GPR | GNR | Y/M | Lot # | AL/ACT # | QC SSN | Comments
2012-07-02 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-06655 | Door to 140, Door to 126, Flame Cab., Cabinet, Chair
2012-07-03 | 159 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-06750 | Cabool, Marlow pump, Window, Chair, WFI box
2012-07-05 | 133 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-06765 | Flam cab., Door to 140, Door to 132, sink, refrig door
2012-07-06 | 156 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-06807 | S. wall, N.wall, N. counter, E. wall, cart
2012-07-09 | 156 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-06834 | Water bath, Chiller, Flam. Cabinet, Column, Cart.
2012-07-10 | 135 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-06953 | Sink, Door to 134, Outside BSC, Fridge, Incubator Shaker
2012-07-11 | 163 | 1 | 1 | 0 | 0 | 1 | 2 | 1 |  |  |  |  | QC-12-07005 | Chair, Phone, Carboy, Man. Gauge, Fan
2012-07-12 | 131 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07045 | Door to 140, Chair, Door to 130, Cabinet, Sink
2012-07-13 | 129 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07108 | Door to 140, Door to 128, Cabinet, Chair, Cart
2012-07-16 | 129 | 0 | 1 | 3 | 0 | 1 | 3 | 2 |  |  |  |  | QC-12-07130 | Flam. Cab, Rack , Centrifuge, Door to 128, Floor scale keypad
2012-07-17 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07169 | Outside BSC, Flam. Cabinet, Door to 140, Cabinet, Window
2012-07-18 | 161 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07207 | Carboy, Column, Canister, Sink pole, PW DV 11
2012-07-19 | 159 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07246 | N. wall, WFI box, W. wall, Window, Flam. Cabinet
2012-07-20 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07314 | Door to 140, Door to 126, Flame Cab., Cabinet, Chair
2012-07-23 | 129 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07396 | Cart, Centrifuge, Carr. Cab, Flam. Cab, Door to 128
2012-07-24 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07438 | Door to 126, Flam. Cabinet, outside BSC, Fridge, Door to 140
2012-07-25 | 156 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07465 | Cart, Cabinet, Carboy, Window, eye wash
2012-07-26 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07511 | Door to 126, Flam. Cabinet, Outside BSC, window, Door to 140
2012-07-27 | 141 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07527 | Door to 151, Cart, Cabinet, Bench, Chair
2012-07-30
2012-07-31 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07598 | Door to 126, Flam. Cabinet,BSC, Window, Door to 140
2012-08-01
2012-08-02 | 156 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07737 | Ice bucket, Chiller, Flam. Cab, Cart, Biohaz container
2012-08-03 | 141 | 0 | 0 | 3 | 0 | 0 | 3 | [5 empty] | QC-12-07765 | Door to 150, Sick, Awoclare, Outside treat, Lancer
2012-08-06 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07778 | Door to 140, Door to 126, Flame Cab., Cabinet, Chair
2012-08-07 | 156 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07802 | Ice bucket, Chiller, Flam. Cab, Pump, Water bath
2012-08-08 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07825 | Door to 126, Door to 140, Flame Cab., Cabinet, Chair
2012-08-09 | 141 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07889 | Lancer, Window, Cabinets, Depyro oven, autoclare
2012-08-10 | 159 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07898 | N. wall, W. wall, WFI box, Window Flam. Cabinet
2012-08-13 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-07957 | Door to 126, Door to 140, Flame Cab., Cabinet, Chair
2012-08-14 | 156 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08007 | Column, Red cart, ( - ) ground, Water bath, Flam cab.
2012-08-15 | 159 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08051 | N.wall, W. wall, WFI box, Window, Flam. Cabinet
2012-08-16 | 133 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08106 | Cabinets, Fridge, Scale, Flam. Cab., Door to 132
2012-08-17 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08160 | Door to 126, Door to 140, Flame Cab., Cabinet, Chair
2012-08-20 | 136 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08246 | S. wall, N. wall, Flam cab., Acid cab., Quar. cab
2012-08-21 | 156 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08259 | Chiller, Flam. Cab., Bionaz container, Column, Tool Cart
2012-08-22 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08311 | Door to 126, Flam. Cabinet, Outside BSC, Window, Fridge
2012-08-23 | 153 | 0 | 1 | 0 | 0 | 0 | 1 | [5 empty] | QC-12-08410 | Tank, Computer station, Bio process system, Pump, Stir plate
2012-08-24 | 163 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08446 | Acid Cab., Flam. Cab., N. Wall, Gas Chromatograph, W. Wall
2012-08-27 | 156 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08532 | Chiller, Water bath, Flam. Cabinet, Buffe container, Window
2012-08-28 | 156 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08570 | Casette holder, Chiller, Flam. Cab., Biohaz cont., Bucket
2012-08-29 | 131 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08628 | Shower, Outside LAF, Scale, Flam. Cab, Door to 130
2012-08-30 | 133 | 0 | 1 | 0 | 0 | 1 |  | 1 |  | 1 |  |  | QC-12-08673 | Outside BSC, Skid, Skid panel, Cabinet, Phone. Large, grey/white/orange mold. GPR w/spores
2012-08-31 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08706 | Door to 140, Door to 126, Flame Cab., Cabinet, Chair
2012-09-04 | 153 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08819 | N. Wall, Centrfuge, Flam. Cab., Chair, Door to 152
2012-09-05 | 163 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08848 | E. wall, W. wall, Gas Chrom., Acid cab., Flam cab.
2012-09-06 | 129 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-08896 | Door to 128, Door to 140, Chair, Carboy, Cart
2012-09-07 | 156 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-09019 | Ice bucket, water bath, Flam. Cab., Chiller, Biohaz. Cont.
2012-09-10 | 141 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-09046 | Door to 151, Door to 139, Cabinet, Chair, Cart
2012-09-11 | 133 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-09154 | Door to 132, AKTA, Fridge, Flame cab., Freezer
2012-09-12 | 131 | 0 | 0 | 0 | 0 | 1 | 1 | [5 empty] | QC-12-09195 | Flam. Cab, Rack, Outside hood, Pole, Waterbath
2012-09-13 | 156 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-09221 | Water bath, Chiller, Column, Flam. Cabinet, Window
2012-09-14 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-09349 | Outside BSC, Eyewash, R2S, Fridge, Flam. Cab
2012-09-17 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-09411 | Door to 140, Door to 126, Flame Cab., Cabinet, Chair
2012-09-18 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-09457 | Refrig door, Door to 140, Door to 126, Flam. Cab, UV spec.
2012-09-19 | 131 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-09485 | Door to 140, Door to 130, Flame Cab., Carboy, Chair
2012-09-20 | 131 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-09544 | Outside LAF, Tube rack, Pump in hood, Scale keypad in hood, Black waste container
2012-09-21 | 163 | 2 | 3 | 0 | 4 | 0 | 7 | 2 |  |  |  |  | QC-12-09571 | Fan, Lyo. PC, Bin, Chair, Flam. Cabinet
2012-09-24 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-09614 | Door to 126, Flam. Cabinet, Outside BSC, Cabinet, Door to 140
2012-09-25 | 127 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-09646 | Door to 140, Door to 126, Flame Cab., Cabinet, Chair
2012-09-26 | 163 | 1 | 0 | 0 | 0 | 0 | 1 | [5 empty] | QC-12-09680 | Cart, RM rack , Tool box, Bin, E. wall
2012-09-27 | 133 | 0 | 0 | 0 | 0 | 0 | [6 empty] | QC-12-09746 | Fridge, Scale, Door to 132, Cabinets, Flam. Cab
2012-09-28 | 156 | 0 | 0 | 0 | 0 | 2 |  | 1 |  | 1 |  |  | QC-12-09815 | Tank 1, Tank 2, Tank 3, Tank 4, Tank 5
| S1: 115; F1: 18; F2: 7 | 0 | 2
Aseptic Core
RM 143/144/145 | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | TAMC | Gram Stain/
Date | S1 | S2 | S3 | S4 | S5 | S6 | F1 | F2 | GPC | GPR | GNR | Y/M | AL/ACT # | QC SSN | Comments
2012-07-02 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-06655
2012-07-03 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-06696
2012-07-10 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-06909
2012-07-13 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07113
2012-07-16 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07122
2012-07-18 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07194
2012-07-23 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07398
2012-07-25 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07466
2012-07-31 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07628 | SDA
2012-07-31 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07627
2012-08-01 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07674
2012-08-07 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07809
2012-08-09 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07894
2012-08-13 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07961
2012-08-16 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08084
2012-08-23 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08416
2012-08-24 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08482
2012-08-28 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08548
2012-08-30 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08683
2012-09-04 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08821
2012-09-05 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08854
2012-09-10 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-09062
2012-09-11 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-09120
2012-09-18 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-09448
2012-09-21 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-09573
2012-09-24 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-09631
2012-09-26 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-09682
2012-07-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06655
2012-07-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06696
2012-07-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-06909
2012-07-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07113
2012-07-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07122
2012-07-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07194
2012-07-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07398
2012-07-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07466
2012-07-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07628 | SDA
2012-07-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07627
2012-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07674
2012-08-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07809
2012-08-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07894
2012-08-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-07961
2012-08-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08084
2012-08-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08416
2012-08-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08482
2012-08-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08548
2012-08-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08683
2012-09-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08821
2012-09-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-08854
2012-09-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09062
2012-09-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09120
2012-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09448
2012-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09573
2012-09-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09631
2012-09-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | QC-12-09682
2012-07-02 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-06655
2012-07-03 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-06696
2012-07-10 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-06909
2012-07-13 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07113
2012-07-16 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07122
2012-07-18 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07194
2012-07-23 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07398
2012-07-25 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07466
2012-07-31 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07628 | SDA
2012-07-31 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07627
2012-08-01 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07674
2012-08-07 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07809
2012-08-09 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07894
2012-08-13 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-07961
2012-08-16 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08084
2012-08-23 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08416
2012-08-24 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08482 |  |  | 130
2012-08-28 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08548 |  |  | 199
2012-08-30 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08683 |  |  | 16
2012-09-04 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08821 |  |  | 215
2012-09-05 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-08854
2012-09-10 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-09062
2012-09-11 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-09120
2012-09-18 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-09448
2012-09-21 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-09573
2012-09-24 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-09631
2012-09-26 | 0 | 0 | 0 | 0 |  |  | 0 | [6 empty] | QC-12-09682
| S1: 486 | 0 | 0 | 0 | 0
Formulas:
RM 119/138/139 = [RM 119/138/139, row above]+1

## Sheet1
Date | TAMC | Alert | Action
2011-11-22 | 0 | 3 | 5
2011-11-29 | 0 | 3 | 5
2011-12-01 | 0 | 3 | 5
2011-12-08 | 0 | 3 | 5
2011-12-06 | 0 | 3 | 5
2011-12-21 | 0 | 3 | 5
2011-12-21 | 0 | 3 | 5
2011-12-16 | 0 | 3 | 5
2011-12-16 | 0 | 3 | 5
2011-12-20 | 0 | 3 | 5
2011-12-20 | 0 | 3 | 5
2011-12-19 | 0 | 3 | 5
2011-12-12 | 0 | 3 | 5
2011-12-30 | 0 | 3 | 5
2012-01-03 | 0 | 3 | 5
2012-01-06 | 0 | 3 | 5
2012-01-09 | 0 | 3 | 5
2012-01-10 | 0 | 3 | 5
2012-01-16 | 0 | 3 | 5
2012-01-24 | 0 | 3 | 5
2012-01-27 | 0 | 3 | 5
2012-01-19 | 0 | 3 | 5
2012-01-19 | 2 | 3 | 5
2012-02-09 | 0 | 3 | 5
2012-02-09 | 7 | 3 | 5
2012-01-31 | 0 | 3 | 5
2012-02-06 | 0 | 3 | 5

## ACT Area 1 Summary
Gowning and Hallways (119, 138, and 139)
Test | Total Samples | Number Over Alert Level | Number Over Action Level | % Over Alert Level | % Over Action Level
Total Particulates at 0.5-µm | 162 | 0 | 0 | 0 | 0
Total Particulates at 5.0-µm | 162 | 0 | 0 | 0 | 0
Air Viables | 58 | 0 | 0 | 0 | 0
Surface and Floor Viables | 220 | 0 | 0 | 0 | 0
Grand Total | 602 | 0 | 0 | 0 | 0

## ACT Area 2 Summary
Circulation Hallway and Airlock (140, 150, and 151)
Test | Total Samples | Number Over Alert Level | Number Over Action Level | % Over Alert Level | % Over Action Level
Total Particulates at 0.5-µm | 120 | 0 | 0 | 0 | 0
Total Particulates at 5.0-µm | 120 | 0 | 0 | 0 | 0
Air Viables | 40 | 1 | 0 | 2.5 | 0
Surface and Floor Viables | 214 | 0 | 0 | 0 | 0
Grand Total | 494 | 1 | 0 | 0.20243 | 0

## ACT Area 3 Summary
Cell Banking 1 (126 and 127)
Test | Total Samples | Number Over Alert Level | Number Over Action Level | % Over Alert Level | % Over Action Level
Total Particulates at 0.5-µm | 381 | 0 | 0 | 0 | 0
Total Particulates at 5.0-µm | 381 | 0 | 0 | 0 | 0
Air Viables | 49 | 2 | 0 | 4.0816 | 0
Surface and Floor Viables | 376 | 1 | 1 | 0.26596 | 0.26596
Grand Total | 1187 | 3 | 1 | 0.25274 | 0.084246

## ACT Area 4 Summary
Fermentation 1 (128 and 129)
Test | Total Samples | Number Over Alert Level | Number Over Action Level | % Over Alert Level | % Over Action Level
Total Particulates at 0.5-µm | 182 | 0 | 0 | 0 | 0
Total Particulates at 5.0-µm | 182 | 1 | 0 | 0.54945 | 0
Air Viables | 75 | 0 | 0 | 0 | 0
Surface and Floor Viables | 195 | 0 | 0 | 0 | 0
Grand Total | 634 | 1 | 0 | 0.15773 | 0

## ACT Area 5 Summary
Fermentation 2 (134 and 135)
Test | Total Samples | Number Over Alert Level | Number Over Action Level | % Over Alert Level | % Over Action Level
Total Particulates at 0.5-µm | 169 | 0 | 0 | 0 | 0
Total Particulates at 5.0-µm | 169 | 0 | 0 | 0 | 0
Air Viables | 70 | 0 | 0 | 0 | 0
Surface and Floor Viables | 182 | 0 | 0 | 0 | 0
Grand Total | 590 | 0 | 0 | 0 | 0

## ACT Area 6 Summary
Purification 3 (153 and 154)
Test | Total Samples | Number Over Alert Level | Number Over Action Level | % Over Alert Level | % Over Action Level
Total Particulates at 0.5-µm | 351 | 6 | 0 | 1.7094 | 0
Total Particulates at 5.0-µm | 351 | 6 | 5 | 1.7094 | 1.4245
Air Viables | 145 | 0 | 0 | 0 | 0
Surface and Floor Viables | 550 | 2 | 1 | 0.36364 | 0.18182
Grand Total | 1397 | 14 | 6 | 1.0021 | 0.42949

## ACT Area 7 Summary
Purification 1 (130 and 131)
Test | Total Samples | Number Over Alert Level | Number Over Action Level | % Over Alert Level | % Over Action Level
Total Particulates at 0.5-µm | 338 | 7 | 2 | 2.071 | 0.59172
Total Particulates at 5.0-µm | 338 | 11 | 7 | 3.2544 | 2.071
Air Viables | 135 | 0 | 0 | 0 | 0
Surface and Floor Viables | 297 | 2 | 1 | 0.6734 | 0.3367
Grand Total | 1108 | 20 | 10 | 1.8051 | 0.90253

## ACT Area 8 Summary
Purification 2 (132 and 133)
Test | Total Samples | Number Over Alert Level | Number Over Action Level | % Over Alert Level | % Over Action Level
Total Particulates at 0.5-µm | 338 | 5 | 1 | 1.4793 | 0.29586
Total Particulates at 5.0-µm | 338 | 8 | 5 | 2.3669 | 1.4793
Air Viables | 135 | 4 | 2 | 2.963 | 1.4815
Surface and Floor Viables | 324 | 0 | 0 | 0 | 0
Grand Total | 1135 | 17 | 8 | 1.4978 | 0.70485

## ACT Area 9 Summary
Cell Banking 2 (152 and 156)
Test | Total Samples | Number Over Alert Level | Number Over Action Level | % Over Alert Level | % Over Action Level
Total Particulates at 0.5-µm | 234 | 0 | 0 | 0 | 0
Total Particulates at 5.0-µm | 234 | 3 | 1 | 1.2821 | 0.42735
Air Viables | 81 | 0 | 0 | 0 | 0
Surface and Floor Viables | 324 | 2 | 0 | 0.61728 | 0
Grand Total | 873 | 5 | 1 | 0.57274 | 0.11455

## ACT Area 10 Summary
Media and Buffer Prep (136 and 137)
Test | Total Samples | Number Over Alert Level | Number Over Action Level | % Over Alert Level | % Over Action Level
Total Particulates at 0.5-µm | 162 | 0 | 0 | 0 | 0
Total Particulates at 5.0-µm | 162 | 0 | 0 | 0 | 0
Air Viables | 58 | 0 | 0 | 0 | 0
Surface and Floor Viables | 145 | 0 | 0 | 0 | 0
Grand Total | 527 | 0 | 0 | 0 | 0

## ACT Area 11 Summary
Glasswash (141)
Test | Total Samples | Number Over Alert Level | Number Over Action Level | % Over Alert Level | % Over Action Level
Total Particulates at 0.5-µm | 141 | 0 | 0 | 0 | 0
Total Particulates at 5.0-µm | 141 | 0 | 0 | 0 | 0
Air Viables | 56 | 0 | 0 | 0 | 0
Surface and Floor Viables | 112 | 0 | 0 | 0 | 0
Grand Total | 450 | 0 | 0 | 0 | 0

## ACT Area 12 Summary
Aseptic Support (143, 144, and 145)
Test | Total Samples | Number Over Alert Level | Number Over Action Level | % Over Alert Level | % Over Action Level
Total Particulates at 0.5-µm | 264 | 0 | 0 | 0 | 0
Total Particulates at 5.0-µm | 264 | 0 | 0 | 0 | 0
Air Viables | 164 | 0 | 0 | 0 | 0
Surface and Floor Viables | 491 | 0 | 0 | 0 | 0
Grand Total | 1183 | 0 | 0 | 0 | 0

## ACT Area 17 Summary
Gowning, Staging, and Formulation (157, 158, and 159)
Test | Total Samples | Number Over Alert Level | Number Over Action Level | % Over Alert Level | % Over Action Level
Total Particulates at 0.5-µm | 260 | 0 | 0 | 0 | 0
Total Particulates at 5.0-µm | 260 | 0 | 0 | 0 | 0
Air Viables | 108 | 0 | 0 | 0 | 0
Surface and Floor Viables | 594 | 0 | 0 | 0 | 0
Grand Total | 1222 | 0 | 0 | 0 | 0

## ACT Area 18 Summary
Buffer Prep 2 (160 and 161)
Test | Total Samples | Number Over Alert Level | Number Over Action Level | % Over Alert Level | % Over Action Level
Total Particulates at 0.5-µm | 117 | 0 | 0 | 0 | 0
Total Particulates at 5.0-µm | 117 | 0 | 0 | 0 | 0
Air Viables | 42 | 0 | 0 | 0 | 0
Surface and Floor Viables | 140 | 0 | 0 | 0 | 0
Grand Total | 416 | 0 | 0 | 0 | 0

## ACT Area 19 Summary
Manufacturing Support Areas (147B, 162, and 163)
Test | Total Samples | Number Over Alert Level | Number Over Action Level | % Over Alert Level | % Over Action Level
Total Particulates at 0.5-µm | 165 | 0 | 0 | 0 | 0
Total Particulates at 5.0-µm | 165 | 0 | 0 | 0 | 0
Air Viables | 59 | 0 | 0 | 0 | 0
Surface and Floor Viables | 250 | 0 | 0 | 0 | 0
Grand Total | 639 | 0 | 0 | 0 | 0